{"text_format":"1","workbook":"xlsx","n_sheets":1,"sheets":["Prototype A20"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":0,"defined_names":20,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Prototype A20","index":0,"n_rows":71,"n_cols":15,"rows_kept":71,"cut":false,"hidden":false,"merged":[[3,5,3,9],[3,10,3,14]]}
[]
["Output Results for Performance Based Code Compliance Reference Design Tests (Envelope Requirements shall use U-Factor for walls and Roofs, and F-Factor for slab-on-grade floors)"]
[]
[null,null,null,null,null,"Test Run 1 (Climate Zone 1)",null,null,null,null,"Test Run 2 (Climate Zone 2)"]
[null,"TYPE","Description of Components","UNITS","MIN / MAX","Sizing Results","Reference Results for Baseline model (ASHRAE)","Compliance Software Baseline Model Results (ASHRAE)","Reference Results for Baseline model (FEC)","Compliance Software Baseline Model Results (FEC)","Sizing Results","Reference Results for Baseline model (ASHRAE)","Compliance Software Baseline Model Results (ASHRAE)","Reference Results for Baseline model (FEC)","Compliance Software Baseline Model Results (FEC)"]
["Envelope Components"]
[null,"Wall","Exterior Wall: U-Value","Btu/(h-ft2-°F)","MAX",null,0.124,0.124,7.6999999999999999E-2,7.6999999999999999E-2,null,0.124,0.124,7.6999999999999999E-2,7.6999999999999999E-2]
[null,"Wall","Exterior Wall: Thermal Capacity","(Btu/ft2-°F)",null,null,3.11,3.11,"NA","NA",null,3.11,3.11,"NA","NA"]
[null,"Wall","Exterior Wall: Solar Reflectance","-","MIN",null,"NA","NA","NR","NR",null,"NA","NA","NR","NR"]
[null,"Wall","Exterior Wall: Solar Absorptance","-","MAX",null,"NA","NA",0.75,0.75,null,"NA","NA",0.75,0.75]
[null,"Wall","Exterior Wall: Thermal Emittance","-","MIN",null,"NA","NA",0.9,0.9,null,"NA","NA",0.9,0.9]
[null,"Floor","Floor Slab-on-grade: Unheated F-factor","Btu/(h-ft-°F)","MAX",null,0.73,0.73,0.73,0.73,null,0.73,0.73,0.73,0.73]
[null,"Floor","Floor Slab-on-grade: Thermal Capacity","(Btu/ft2-°F)",null,null,9.33,9.33,"NA","NA",null,9.33,9.33,"NA","NA"]
[null,"Roof","Exterior Roof: U-Value","Btu/(h-ft2-°F)","MAX",null,6.3E-2,6.3E-2,4.8000000000000001E-2,4.8000000000000001E-2,null,4.8000000000000001E-2,4.8000000000000001E-2,4.8000000000000001E-2,4.8000000000000001E-2]
[null,"Roof","Exterior Roof: Thermal Capacity","(Btu/ft2-°F)",null,null,2.7,2.7,"NA","NA",null,2.7,2.7,"NA","NA"]
[null,"Roof","Exterior Roof: Solar Reflectance","-","MIN",null,0.55000000000000004,0.55000000000000004,"NA","NA",null,0.55000000000000004,",55","NA","NA"]
[null,"Roof","Exterior Roof: Solar Absorptance","-","MAX",null,"NR","NR",0.75,0.75,null,"NR","NR",0.75,0.75]
[null,"Roof","Exterior Roof: Thermal Emittance","-","MIN",null,0.9,0.9,0.9,0.9,null,0.9,0.9,0.9,0.9]
[null,"Floor","Internal Floor: Thermal Capacity","(Btu/ft2-°F)",null,null,"NC","NC","NA","NA",null,"NC","NC","NA","NA"]
[null,"Floor","Internal Floor: U-Value","Btu/(h-ft2-°F)","MAX",null,"NC","NC","NC","NC",null,"NC","NC","NC","NC"]
[null,"Fenestration","Exterior Window: U-Value","Btu/(h-ft2-°F)","MAX",null,1.2,1.2,0.5,0.5,null,0.75,0.75,0.5,0.5]
[null,"Fenestration","Exterior Window: SHGC","-","MAX",null,0.25,0.25,0.25,0.25,null,0.25,0.25,0.25,0.25]
[null,"Fenestration","Exterior Window: WWR","(%)","Max",null,40,0.2833,40,0.28299999999999997,null,40,0.28299999999999997,40,0.28299999999999997]
[null,"Fenestration","Window Area"]
[null,"Fenestration","South Window Area","ft2","MAX",null,14440,1530,14440,1530,null,14440,1530,14440,1530]
[null,"Fenestration","East Window Area","ft2","MAX",null,14440,1530,14440,1530,null,14440,1530,14440,1530]
[null,"Fenestration","North Window Area","ft2","MAX",null,14440,1530,14440,1530,null,14440,1530,14440,1530]
[null,"Fenestration","West Window Area","ft2","MAX",null,14440,1530,14440,1530,null,14440,1530,14440,1530]
[null,"Skylight","Skylight Area","ft2","MAX",null,"NA","NA","NA","NA",null,"NA","NA","NA","NA"]
[null,"Skylight","Skylight: U-Value","Btu/(h-ft2-°F)","MAX",null,"NA","NA","NA","NA",null,"NA","NA","NA","NA"]
[null,"Skylight","Skylight: SHGC","-","MAX",null,"NA","NA","NA","NA",null,"NA","NA","NA","NA"]
[null,"Skylight","Skylight: Skylight-Roof Ratio","(%)","MAX"]
[]
["Interior Lighting"]
[null,"Lighting","LPD: Building Area Method","W/ft2","MAX",null,0.9,0.9,0.9,0.9,null,0.9,0.9,0.9,0.9]
[null,null,null,null,""]
["Exterior Lighting",null,null,null,""]
[null,"Lighting","Total Lighting Allowance (W)","W","MAX",null,1450,1450,1450,1450,null,1450,1450,1450,1450]
[null,null,null,null,""]
["Internal Loads"]
[null,"Equipment","Internal Electric Power Density","W/ft2","-",null,1,"NC",1,"NC",null,1,"NC",1,"NC"]
[]
["HVAC System"]
[null,null,"HVAC system type",null,null,null,"VAV with Reheat, Chilled Water, Hot-Water Fossil Fuel Boiler",null,"VAV with Reheat, Chilled Water, Hot-Water Fossil Fuel Boiler",null,null,"VAV with Reheat, Chilled Water, Hot-Water Fossil Fuel Boiler",null,"VAV with Reheat, Chilled Water, Hot-Water Fossil Fuel Boiler"]
[]
[null,null,"Boiler Minimum Heating Efficiency:"]
[null,"Oil Boiler","Oil-Fired Boiler Efficiency: ASHRAE","% AFUE","MIN",180,80,80,null,null,330,82,82]
[null,"Oil Boiler","Oil-Fired Boiler Efficiency: FEC","% AFUE","MIN",140,null,null,80,80,260,null,null,80,80]
[]
[]
[null,null,"Water Chilling Package Minimum Efficiency:"]
[null,null,"Electrically Operated: "]
[null,null,"Path A: Centrifugal"]
[null,"Chiller","Central Centrifugal Chiller Efficiency: ASHRAE","kW/ton","MIN",766.58,"0.570 kW/ton, 0.539 IPLV","0.570 kW/ton, 0.539 IPLV",null,null,715.41,"0.570 kW/ton, 0.539 IPLV","0.570 kW/ton, 0.539 IPLV"]
[null,"Chiller","Central Centrifugal Chiller Efficiency: FEC","kW/ton","MIN",920,null,null,"0.570 kW/ton, 0.539 IPLV","0.570 kW/ton, 0.539 IPLV",709.58,null,null,"0.570 kW/ton, 0.539 IPLV","0.570 kW/ton, 0.539 IPLV"]
[]
[]
[null,null,"Air Economizer Requirement (Yes, or No):"]
[null,"Air Economizer","First Floor System Economizer: ASHRAE ","-","-",959.13400000000001,"No","NA",null,null,989.71199999999999,"Yes","NA"]
[null,"Air Economizer","First Floor System Economizer: FEC","-","-",938.77800000000002,null,null,"No","NA",980.12900000000002,null,null,"Yes","NA"]
[]
[null,"Air Economizer","Mid Floors (2-19) System Economizer: ASHRAE ","-","-",5244.9589999999998,"No","NA",null,null,5137.799,"Yes","NA"]
[null,"Air Economizer","Mid Floors (2-19) System Economizer: FEC","-","-",5216.0969999999998,null,null,"No","NA",5119.1790000000001,null,null,"Yes","NA"]
[]
[null,"Air Economizer","Top Floor System Economizer: ASHRAE ","-","-",571.93499999999995,"No","NA",null,null,558.26499999999999,"Yes","NA"]
[null,"Air Economizer","Top Floor System Economizer: FEC","-","-",543.87300000000005,null,null,"No","NA",539.947,null,null,"Yes","NA"]
[]
[]
["Elevator Motor"]
[null,null,"Electric Motor Power (HP)","HP","MAX",null,20,"NA",20,"NA",null,20,"NA",20,"NA"]
[null,null,"Electric Motor Efficiency (%)","%","MAX",null,92,"NA",92,"NA",null,92,"NA",92,"NA"]