{"text_format":"1","workbook":"xlsx","n_sheets":1,"sheets":["Prototype A3"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":0,"defined_names":20,"comments":1,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Prototype A3","index":0,"n_rows":83,"n_cols":15,"rows_kept":83,"cut":false,"hidden":false,"merged":[[3,10,3,14],[3,5,3,9]]}
[]
["Output Results for Performance Based Code Compliance Reference Design Tests (Envelope Requirements shall use U-Factor for walls and Roofs, and F-Factor for slab-on-grade floors)"]
[]
[null,null,null,null,null,"Test Run 1 (Climate Zone 1)",null,null,null,null,"Test Run 2 (Climate Zone 2)"]
[null,"TYPE","Description of Components","UNITS","MIN / MAX","Sizing Results","Reference Results for Baseline model (ASHRAE)","Compliance Software Baseline Model Results (ASHRAE)","Reference Results for Baseline model (FEC)","Compliance Software Baseline Model Results (FEC)","Sizing Results","Reference Results for Baseline model (ASHRAE)","Compliance Software Baseline Model Results (ASHRAE)","Reference Results for Baseline model (FEC)","Compliance Software Baseline Model Results (FEC)"]
["Envelope Components"]
[null,"Wall","Exterior Wall: U-Value","Btu/(h-ft2-°F)","MAX",null,0.124,0.124,7.6999999999999999E-2,7.6999999999999999E-2,null,0.124,0.124,7.6999999999999999E-2,7.6999999999999999E-2]
[null,"Wall","Exterior Wall: Thermal Capacity","(Btu/ft2-°F)",null,null,3.11,3.11,"NA","NA",null,3.11,3.11,"NA","NA"]
[null,"Wall","Exterior Wall: Solar Reflectance","-","MIN",null,"NA","NA","NR","NR",null,"NA","NA","NR","NR"]
[null,"Wall","Exterior Wall: Solar Absorptance","-","MAX",null,"NA","NA",0.75,0.75,null,"NA","NA",0.75,0.75]
[null,"Wall","Exterior Wall: Thermal Emittance","-","MIN",null,"NA","NA",0.9,0.9,null,"NA","NA",0.9,0.9]
[null,"Floor","Floor Slab-on-grade: Unheated F-factor","Btu/(h-ft-°F)","MAX",null,0.73,0.73,0.73,0.73,null,0.73,0.73,0.73,0.73]
[null,"Floor","Floor Slab-on-grade: Thermal Capacity","(Btu/ft2-°F)",null,null,9.33,9.33,"NA","NA",null,9.33,9.33,"NA","NA"]
[null,"Roof","Exterior Roof: U-Value","Btu/(h-ft2-°F)","MAX",null,6.3E-2,6.3E-2,4.8000000000000001E-2,4.8000000000000001E-2,null,4.8000000000000001E-2,4.8000000000000001E-2,4.8000000000000001E-2,4.8000000000000001E-2]
[null,"Roof","Exterior Roof: Thermal Capacity","(Btu/ft2-°F)",null,null,2.7,2.7,"NA","NA",null,2.7,2.7,"NA","NA"]
[null,"Roof","Exterior Roof: Solar Reflectance","-","MIN",null,0.55000000000000004,0.55000000000000004,"NA","NA",null,0.55000000000000004,0.55000000000000004,"NA","NA"]
[null,"Roof","Exterior Roof: Solar Absorptance","-","MAX",null,"NR","NR",0.75,0.75,null,"NR","NR",0.75,0.75]
[null,"Roof","Exterior Roof: Thermal Emittance","-","MIN",null,0.75,0.75,0.9,0.9,null,0.9,0.9,0.9,0.9]
[null,"Floor","Internal Floor: Thermal Capacity","(Btu/ft2-°F)",null,null,8.3800000000000008,"NC","NA","NA",null,8.3800000000000008,"NC","NA","NA"]
[null,"Floor","Internal Floor: U-Value","Btu/(h-ft2-°F)","MAX",null,0.33200000000000002,"NC",6.6000000000000003E-2,"NC",null,0.107,"NC",3.3000000000000002E-2,"FAIL (0.62)"]
[null,"Fenestration","Exterior Window: U-Value","Btu/(h-ft2-°F)","MAX",null,1.2,1.2,0.5,0.5,null,0.75,0.75,0.5,0.5]
[null,"Fenestration","Exterior Window: SHGC","-","MAX",null,0.25,0.25,0.25,0.25,null,0.25,0.25,0.25,0.25]
[null,"Fenestration","Exterior Window: WWR","(%)","Max",null,28,0.28000000000000003,28,0.28000000000000003,null,28,0.28000000000000003,28,0.28000000000000003]
[null,"Fenestration","Window Area"]
[null,"Fenestration","South Window Area","ft2","MAX",null,1650,1650,1650,1650,null,1650,1650,1650,1650]
[null,"Fenestration","East Window Area","ft2","MAX",null,1650,1650,1650,1650,null,1650,1650,1650,1650]
[null,"Fenestration","North Window Area","ft2","MAX",null,1650,1650,1650,1650,null,1650,1650,1650,1650]
[null,"Fenestration","West Window Area","ft2","MAX",null,1650,1650,1650,1650,null,1650,1650,1650,1650]
[null,"Skylight","Skylight Area","ft2","MAX",null,"NA","NA","NA","NA",null,"NA","NA","NA","NA"]
[null,"Skylight","Skylight: U-Value","Btu/(h-ft2-°F)","MAX",null,"NA","NA","NA","NA",null,"NA","NA","NA","NA"]
[null,"Skylight","Skylight: SHGC","-","MAX",null,"NA","NA","NA","NA",null,"NA","NA","NA","NA"]
[null,"Skylight","Skylight: Skylight-Roof Ratio","(%)","MAX",null,null,"NA"]
[]
["Interior Lighting"]
[null,"Lighting","LPD: Building Area Method","W/ft2","MAX",null,0.9,0.9,0.9,0.9,null,0.9,0.9,0.9,0.9]
[null,null,null,null,""]
["Exterior Lighting",null,null,null,""]
[null,"Lighting","Total Lighting Allowance (W)","W","MAX",null,870,870,870,870,null,870,870,870,870]
[null,null,null,null,""]
["Internal Loads"]
[null,"Equipment","Internal Electric Power Density","W/ft2","-",null,1,"NC",1,"NC",null,1,"FAIL (1.5)",1,"FAIL (1.5)"]
[]
["HVAC System"]
[null,null,"HVAC System Type",null,null,null,"Packaged VAV with reheat, DX, Fossil Fuel HotWater Boiler",null,"Packaged VAV with reheat, DX, Fossil Fuel HotWater Boiler",null,null,"Packaged VAV with reheat, DX, Fossil Fuel HotWater Boiler",null,"Packaged VAV with reheat, DX, Fossil Fuel HotWater Boiler"]
[]
[null,null,"Boiler Minimum Heating Efficiency:"]
[null,"Gas Boiler","Gas-Fired Boiler Efficiency: ASHRAE","% Et","MIN",350,80,80,null,null,570,80,80]
[null,"Gas Boiler","Gas-Fired Boiler Efficiency: FEC","% AFUE","MIN",270,null,null,80,80,460,null,null,80,"FAIL (82)"]
[]
[]
[null,null,"Cooling Minimum Efficiency:"]
[null,"Cooling DX","First Floor System Efficiency: ASHRAE","EER / IEER","MIN",922.14200000000005,"9.5 / 9.6","9.5/9.6",null,null,952.77099999999996,"9.5 / 9.6","9.5/9.6"]
[null,"Cooling DX","First Floor System Efficiency: FEC","EER / IEER","MIN",905.74199999999996,null,null,"9.5 / 9.6","9.5/9.6",943.74,null,null,"9.5 / 9.6","FAIL (9.7/9.2)"]
[]
[null,"Cooling DX","Mid Floor System Efficiency: ASHRAE","EER / IEER","MIN",633.27800000000002,"9.8 / 9.9","9.8/9.9",null,null,627.19200000000001,"9.8 / 9.9","9.8/9.9"]
[null,"Cooling DX","Mid Floor System Efficiency: FEC","EER / IEER","MIN",609.86800000000005,null,null,"9.8 / 9.9","9.8/9.9",610.96600000000001,null,null,"9.8 / 9.9","10.0/10.1"]
[]
[null,"Cooling DX","Top Floor System Efficiency: ASHRAE","EER / IEER","MIN",653.63699999999994,"9.8 / 9.9","9.8/9.9",null,null,639.13699999999994,"9.8 / 9.9","9.8/9.9"]
[null,"Cooling DX","Top Floor System Efficiency: FEC","EER / IEER","MIN",627.23299999999995,null,null,"9.8 / 9.9","9.8/9.9",628.35900000000004,null,null,"9.8 / 9.9","10.0/10.1"]
[]
[]
[null,null,"Air Economizer Requirement (Yes, or No):"]
[null,"Air Economizer","First Floor System Economizer: ASHRAE ","-","-",{"$f":"FirstFloorCoolCap","v":922.14200000000005},"No","NA",null,null,{"$f":"FirstFloorCoolCapCZ2","v":952.77099999999996},"Yes","NA"]
[null,"Air Economizer","First Floor System Economizer: FEC","-","-",{"$f":"FirstFloorCoolCapIECC","v":905.74199999999996},null,null,"No","NA",{"$f":"FirstFloorCoolCapIECCCZ2","v":943.74},null,null,"Yes","NA"]
[]
[null,"Air Economizer","Mid Floor System Economizer: ASHRAE ","-","-",{"$f":"MidFloorCoolCap","v":633.27800000000002},"No","NA",null,null,{"$f":"MidFloorCoolCapCZ2","v":627.19200000000001},"Yes","NA"]
[null,"Air Economizer","Mid Floor System Economizer: FEC","-","-",{"$f":"MidFloorCoolCapIECC","v":609.86800000000005},null,null,"No","NA",{"$f":"MidFloorCoolCapIECCCZ2","v":610.96600000000001},null,null,"Yes","NA"]
[]
[null,"Air Economizer","Top Floor System Economizer: ASHRAE ","-","-",{"$f":"TopFloorCoolCap","v":653.63699999999994},"No","NA",null,null,{"$f":"TopFloorCoolCapCZ2","v":639.13699999999994},"Yes","NA"]
[null,"Air Economizer","Top Floor System Economizer: FEC","-","-",{"$f":"TopFloorCoolCapIECC","v":627.23299999999995},null,null,"No","NA",{"$f":"TopFloorCoolCapIECCCZ2","v":628.35900000000004},null,null,"Yes","NA"]
[]
[]
["Service Water Heating"]
[null,"SWH","SWH Type",null,null,null,"Storage Water Heater",null,"Storage Water Heater",null,null,"Storage Water Heater",null,"Storage Water Heater"]
[null,"SWH","Fuel Type",null,null,null,"Gas",null,"Gas",null,null,"Gas",null,"Gas"]
[null,"SWH","Thermal Efficiency:"]
[null,"SWH","Size <= 75 kBtu/h, Energy Factor (EF)"," - ","MIN",75,0.51800000000000002,0.51800000000000002,0.51800000000000002,0.51800000000000002,77]
[null,"SWH","Size > 75 kBtu/h, Thermal Efficiency (Et)","%","MIN",{"$f":"SWHCapacity","v":75},null,null,null,null,{"$f":"SWHCapacityCZ2","v":77},80,80,80,80]
[]
[]
["Elevator Motor"]
[null,null,"Electric Motor Power (HP)","HP","MAX",null,7.5,"NA",7.5,"NA",null,7.5,"NA",7.5,"NA"]
[null,null,"Electric Motor Efficiency (%)","%","MIN",null,88,"NA",88,"NA",null,88,"NA",88,"NA"]