{"text_format":"1","workbook":"xlsx","n_sheets":1,"sheets":["Prototype C1"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":0,"defined_names":66,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Prototype C1","index":0,"n_rows":122,"n_cols":25,"rows_kept":122,"cut":false,"hidden":false,"merged":[[3,10,3,14],[3,20,3,24],[3,5,3,9],[3,15,3,19]]}
[]
["Output Results for Performance Based Code Compliance Reference Design Tests (Envelope Requirements shall use U-Factor for walls and Roofs, and F-Factor for slab-on-grade floors)"]
[]
[null,null,null,null,null,"Test Run 1 (Climate Zone 1), Manufacturing",null,null,null,null,"Test Run 2 (Climate Zone 2), Manufacturing",null,null,null,null,"Test Run 3 (Climate Zone 1), Warehouse",null,null,null,null,"Test Run 4 (Climate Zone 2), Warehouse"]
[null,"TYPE","Description of Components","UNITS","MIN / MAX","Sizing Results","Reference Results for Baseline model (ASHRAE)","Compliance Software Baseline Model Results (ASHRAE)","Reference Results for Baseline model (FEC)","Compliance Software Baseline Model Results (FEC)","Sizing Results","Reference Results for Baseline model (ASHRAE)","Compliance Software Baseline Model Results (ASHRAE)","Reference Results for Baseline model (FEC)","Compliance Software Baseline Model Results (FEC)","Sizing Results","Reference Results for Baseline model (ASHRAE)","Compliance Software Baseline Model Results (ASHRAE)","Reference Results for Baseline model (FEC)","Compliance Software Baseline Model Results (FEC)","Sizing Results","Reference Results for Baseline model (ASHRAE)","Compliance Software Baseline Model Results (ASHRAE)","Reference Results for Baseline model (FEC)","Compliance Software Baseline Model Results (FEC)"]
["Envelope Components"]
[null,"Wall","Exterior Wall: U-Value","Btu/(h-ft2-°F)","MAX",null,0.57999999999999996,0.57999999999999996,0.14199999999999999,0.14199999999999999,null,0.151,0.151,0.14199999999999999,0.14199999999999999,null,0.57999999999999996,0.57999999999999996,0.14199999999999999,0.14199999999999999,null,0.151,0.151,0.14199999999999999,0.14199999999999999]
[null,"Wall","Exterior Wall: Thermal Capacity","(Btu/ft2-°F)",null,null,21.5,21.5,"NA","NA",null,21.5,21.5,"NA","NA",null,21.5,21.5,"NA","NA",null,21.5,21.5,"NA","NA"]
[null,"Wall","Exterior Wall: Solar Reflectance","-","MIN",null,"NA","NA","NR","NR",null,"NA","NA","NR","NR",null,"NA","NA","NR","NR",null,"NA","NA","NR","NR"]
[null,"Wall","Exterior Wall: Solar Absorptance","-","MAX",null,"NA","NA",0.75,0.75,null,"NA","NA",0.75,0.75,null,"NA","NA",0.75,0.75,null,"NA","NA",0.75,0.75]
[null,"Wall","Exterior Wall: Thermal Emittance","-","MIN",null,"NA","NA",0.9,0.9,null,"NA","NA",0.9,0.9,null,"NA","NA",0.9,0.9,null,"NA","NA",0.9,0.9]
[null,"Floor","Floor Slab-on-grade: Unheated F-factor","Btu/(h-ft-°F)","MAX",null,0.73,0.73,0.73,0.73,null,0.73,0.73,0.73,0.73,null,0.73,0.73,0.73,0.73,null,0.73,0.73,0.73,0.73]
[null,"Floor","Floor Slab-on-grade: Thermal Capacity","(Btu/ft2-°F)",null,null,8.25,8.25,"NA","NA",null,8.25,8.25,"NA","NA",null,8.25,8.25,"NA","NA",null,8.25,8.25,"NA","NA"]
[null,"Roof","Exterior Roof: U-Value","Btu/(h-ft2-°F)","MAX",null,6.3E-2,6.3E-2,4.8000000000000001E-2,4.8000000000000001E-2,null,4.8000000000000001E-2,4.8000000000000001E-2,4.8000000000000001E-2,4.8000000000000001E-2,null,6.3E-2,6.3E-2,4.8000000000000001E-2,4.8000000000000001E-2,null,4.8000000000000001E-2,4.8000000000000001E-2,4.8000000000000001E-2,4.8000000000000001E-2]
[null,"Roof","Exterior Roof: Thermal Capacity","(Btu/ft2-°F)",null,null,2.83,2.83,"NA","NA",null,2.83,2.83,"NA","NA",null,2.83,2.83,"NA","NA",null,2.83,2.83,"NA","NA"]
[null,"Roof","Exterior Roof: Solar Reflectance","-","MIN",null,0.55000000000000004,0.55000000000000004,"NA","NA",null,0.55000000000000004,0.55000000000000004,"NA","NA",null,0.6,0.55000000000000004,"NA","NA",null,0.55000000000000004,0.55000000000000004,"NA","NA"]
[null,"Roof","Exterior Roof: Solar Absorptance","-","MAX",null,"NR","NR",0.75,0.75,null,"NR","NR",0.75,0.75,null,"NR","NR",0.75,0.75,null,"NR","NR",0.75,0.75]
[null,"Roof","Exterior Roof: Thermal Emittance","-","MIN",null,0.9,0.9,0.9,0.9,null,0.9,0.9,0.9,0.9,null,0.9,0.9,0.9,0.9,null,0.9,0.9,0.9,0.9]
[null,"Fenestration","Exterior Window: U-Value","Btu/(h-ft2-°F)","MAX",null,1.2,1.2,0.5,0.5,null,0.75,0.75,0.5,0.5,null,1.2,1.2,0.5,0.5,null,0.75,0.75,0.5,0.5]
[null,"Fenestration","Exterior Window: SHGC","-","MAX",null,0.25,0.25,0.25,0.25,null,0.25,0.25,0.25,0.25,null,0.25,0.25,0.25,0.25,null,0.25,0.25,0.25,0.25]
[null,"Fenestration","Exterior Window: WWR","(%)","Max",null,40,1.6500000000000001E-2,40,1.7000000000000001E-2,null,40,1.7000000000000001E-2,40,1.7000000000000001E-2,null,40,1.7000000000000001E-2,40,1.7000000000000001E-2,null,40,1.7000000000000001E-2,40,1.7000000000000001E-2]
[null,"Fenestration","Window Area"]
[null,"Fenestration","South Window Area","ft2","MAX",null,1280,1280,1280,1280,null,1280,1280,1280,1280,null,1280,1280,1280,1280,null,1280,1280,1280,1280]
[null,"Fenestration","East Window Area","ft2","MAX",null,0,0,0,0,null,0,0,0,0,null,0,0,0,0,null,0,0,0,0]
[null,"Fenestration","North Window Area","ft2","MAX",null,0,0,0,0,null,0,0,0,0,null,0,0,0,0,null,0,0,0,0]
[null,"Fenestration","West Window Area","ft2","MAX",null,0,0,0,0,null,0,0,0,0,null,0,0,0,0,null,0,0,0,0]
[null,"Skylight","Skylight Area","ft2","MAX",null,3200,1850,3200,1110,null,3200,1850,3200,1110,null,3200,1850,3200,1110,null,3200,1850,3200,1110]
[null,"Skylight","Skylight: U-Value","Btu/(h-ft2-°F)","MAX",null,1.98,1.98,0.75,0.75,null,1.98,1.98,0.65,0.65,null,1.98,1.98,0.75,0.75,null,1.98,1.98,0.65,0.65]
[null,"Skylight","Skylight: SHGC","-","MAX",null,0.19,0.19,0.35,0.35,null,0.19,0.19,0.35,0.35,null,0.19,0.19,0.35,0.35,null,0.19,0.19,0.35,0.35]
[null,"Skylight","Skylight: Skylight-Roof Ratio","(%)","MAX",null,5,1.1599999999999999E-2,2,6.94E-3,null,2,1.2E-2,2,6.8999999999999999E-3,null,2,1.2E-2,2,6.8999999999999999E-3,null,2,1.2E-2,2,0.69]
[null,null," "]
["Horizontal Overhang Shade"]
[null,null,"Projection Factor  (-)",null,null,null,0,0,0,0,null,0,0,0,0,null,0,0,0,0,null,0,0,0,0]
[]
["Interior Lighting"]
[null,"Lighting","LPD: Building Area Method","W/ft2","MAX",null,1.1100000000000001,1.1100000000000001,1.3,1.3,null,1.1100000000000001,1.1100000000000001,1.3,1.3,null,0.66,0.66,0.6,0.6,null,0.66,0.66,0.6,0.6]
[null,null,null,null,""]
["Exterior Lighting",null,null,null,""]
[null,"Lighting","Total Lighting Allowance (W)","W","MAX",null,880,880,880,880,null,880,880,880,880,null,880,880,880,880,null,880,880,880,880]
[null,null,null,null,""]
["Internal Loads"]
[null,"Equipment","Internal Electric Power Density","W/ft2","-",null,1.6,"NC",1.6,"NC",null,1.6,"NC",1.6,"NC",null,1,"NC",1,"NC",null,1,"NC",1,"NC"]
[]
["HVAC System"]
[null,null,"HVAC System Type",null,null,null,"Packaged Roof Top Air Conditioner",null,"Packaged Roof Top Air Conditioner",null,null,"Packaged Roof Top Air Conditioner",null,"Packaged Roof Top Air Conditioner",null,null,"Packaged Roof Top Heat Pump",null,"Packaged Roof Top Heat Pump",null,null,"Packaged Roof Top Heat Pump",null,"Packaged Roof Top Heat Pump"]
[]
[null,null,"Minimum Heating Efficiency:"]
[null,null,"Warm-Air Furnace, Gas Fired Efficiency:"]
[null,"Furnace","North Zone Furnace Efficiency: ASHRAE","%AFUE / % ","MIN",392.25,"78.0 / 80.0",80,null,null,305.2,"78.0 / 80.0",80,null,null,null,"NA",null,null,null,null,"NA"]
[null,"Furnace","North Zone Furnace Efficiency: FEC","%AFUE","MIN",310.82,null,null,80,80,233.93,null,null,80,80,null,null,null,"NA",null,null,null,null,"NA"]
[]
[null,"Furnace","South Zone Furnace Efficiency: ASHRAE","%AFUE / % ","MIN",412.53,"78.0 / 80.0",80,null,null,402.88,"78.0 / 80.0",80,null,null,null,"NA",null,null,null,null,"NA"]
[null,"Furnace","South Zone Furnace Efficiency: FEC","%AFUE","MIN",336.21,null,null,80,80,281.33,null,null,80,80,null,null,null,"NA",null,null,null,null,"NA"]
[]
[null,"Furnace","East Zone Furnace Efficiency: ASHRAE","%AFUE / % ","MIN",502.08,"78.0 / 80.0",80,null,null,334.7,"78.0 / 80.0",80,null,null,null,"NA",null,null,null,null,"NA"]
[null,"Furnace","East Zone Furnace Efficiency: FEC","%AFUE","MIN",335.96,null,null,80,80,259.08,null,null,80,80,null,null,null,"NA",null,null,null,null,"NA"]
[]
[null,"Furnace","West Zone Furnace Efficiency: ASHRAE","%AFUE / % ","MIN",474.76,"78.0 / 80.0",80,null,null,343.42,"78.0 / 80.0",80,null,null,null,"NA",null,null,null,null,"NA"]
[null,"Furnace","West Zone Furnace Efficiency: FEC","%AFUE","MIN",334.44,null,null,80,80,257.57,null,null,80,80,null,null,null,"NA",null,null,null,null,"NA"]
[]
[null,"Furnace","Core Zone Furnace Efficiency: ASHRAE","%","MIN",1905.24,80,80,null,null,1968.83,80,80,null,null,null,"NA",null,null,null,null,"NA"]
[null,"Furnace","Core Zone Furnace Efficiency: FEC","%","MIN",1949.36,null,null,80,80,1402.62,null,null,80,80,null,null,null,"NA",null,null,null,null,"NA"]
[]
[]
[null,null,"Heating Minimum Efficiency:"]
[null,null,"Efficiency (HSPF, COP at 47°F/COP at 17°F):"]
[null,"Heating DX","North Zone System Efficiency: ASHRAE","COP / COP","MIN",null,null,null,null,null,null,null,null,null,null,{"$f":"T3CoolCapNorthZone","v":229.11799999999999},"3.2 / 2.05",3.2,null,null,{"$f":"T4CoolCapNorthZone","v":175.67599999999999},"3.2 / 2.05",3.2]
[null,"Heating DX","North Zone System Efficiency: FEC","COP / COP","MIN",null,null,null,null,null,null,null,null,null,null,{"$f":"T3CoolCapNorthZoneIECC","v":173.15299999999999},null,null,"3.2 / 2.05",3.2,{"$f":"T4CoolCapNorthZoneIECC","v":174.999},null,null,"3.2 / 2.05",3.2]
[]
[null,"Heating DX","South Zone System Efficiency: ASHRAE","COP / COP","MIN",null,null,null,null,null,null,null,null,null,null,{"$f":"T3CoolCapSouthZone","v":253.03},"3.2 / 2.05",3.2,null,null,{"$f":"T4CoolCapSouthZone","v":221.23},"3.2 / 2.05",3.2]
[null,"Heating DX","South Zone System Efficiency: FEC","COP / COP","MIN",null,null,null,null,null,null,null,null,null,null,{"$f":"T3CoolCapSouthZoneIECC","v":203.761},null,null,"3.2 / 2.05",3.2,{"$f":"T4CoolCapSouthZoneIECC","v":219.21199999999999},null,null,"3.2 / 2.05",3.2]
[]
[null,"Heating DX","East Zone System Efficiency: ASHRAE","COP / COP","MIN",null,null,null,null,null,null,null,null,null,null,{"$f":"T3CoolCapEastZone","v":284.64100000000002},"3.2 / 2.05",3.2,null,null,{"$f":"T4CoolCapEastZone","v":188.43700000000001},"3.2 / 2.05",3.2]
[null,"Heating DX","East Zone System Efficiency: FEC","COP / COP","MIN",null,null,null,null,null,null,null,null,null,null,{"$f":"T3CoolCapEastZoneIECC","v":192.791},null,null,"3.2 / 2.05",3.2,{"$f":"T4CoolCapEastZone","v":188.43700000000001},null,null,"3.2 / 2.05",3.2]
[]
[null,"Heating DX","West Zone System Efficiency: ASHRAE","COP / COP","MIN",null,null,null,null,null,null,null,null,null,null,{"$f":"T3CoolCapWestZone","v":282.274},"3.2 / 2.05",3.2,null,null,{"$f":"T4CoolCapWestZone","v":198.38},"3.2 / 2.05",3.2]
[null,"Heating DX","West Zone System Efficiency: FEC","COP / COP","MIN",null,null,null,null,null,null,null,null,null,null,{"$f":"T3CoolCapWestZoneIECC","v":185.125},null,null,"3.2 / 2.05",3.2,{"$f":"T4CoolCapWestZoneIECC","v":200.19300000000001},null,null,"3.2 / 2.05",3.2]
[]
[null,"Heating DX","Core Zone System Efficiency: ASHRAE","COP / COP","MIN",null,null,null,null,null,null,null,null,null,null,{"$f":"T3CoolCapCoreZone","v":3766.172},"3.2 / 2.05",3.2,null,null,{"$f":"T4CoolCapCoreZone","v":3823.4569999999999},"3.2 / 2.05",3.2]
[null,"Heating DX","Core Zone System Efficiency: FEC","COP / COP","MIN",null,null,null,null,null,null,null,null,null,null,{"$f":"T3CoolCapCoreZoneIECC","v":3705.4160000000002},null,null,"3.2 / 2.05",3.2,{"$f":"T4CoolCapCoreZoneIECC","v":3862.5320000000002},null,null,"3.2 / 2.05",3.2]
[]
[]
[null,null,"Cooling Minimum Efficiency:"]
[null,"Cooling DX","North Zone System Efficiency: ASHRAE","EER / IEER","MIN",233.42,"10.8 / 11.0","10.8/11",null,null,189.48599999999999,"10.8 / 11.0","10.8/11",null,null,229.11799999999999,"10.8 / 11.0","10.8 / 11.0",null,null,175.67599999999999,"10.8 / 11.0","10.8 / 11.0"]
[null,"Cooling DX","North Zone System Efficiency: FEC","EER / IEER","MIN",193.547,null,null,"10.8 / 11.0","10.8 / 11.0",196.292,null,null,"10.8 / 11.0","10.8 / 11.0",173.15299999999999,null,null,"10.8 / 11.0","10.8 / 11.0",174.999,null,null,"10.8 / 11.0","10.8 / 11.0"]
[]
[null,"Cooling DX","South Zone System Efficiency: ASHRAE","EER / IEER","MIN",251.98400000000001,"9.8 / 9.9","9.8/9.9",null,null,237.541,"10.8 / 11.0","10.8/11",null,null,253.03,"9.8 / 9.9","9.8 / 9.9",null,null,221.23,"10.8 / 11.0","10.8 / 11.0"]
[null,"Cooling DX","South Zone System Efficiency: FEC","EER / IEER","MIN",214.25,null,null,"10.8 / 11.0","10.8 / 11.0",240.49199999999999,null,null,"9.8 / 9.9","9.8 / 9.9",203.761,null,null,"10.8 / 11.0","10.8 / 11.0",219.21199999999999,null,null,"10.8 / 11.0","10.8 / 11.0"]
[]
[null,"Cooling DX","East Zone System Efficiency: ASHRAE","EER / IEER","MIN",296.26400000000001,"9.8 / 9.9","9.8/9.9",null,null,204.035,"10.8 / 11.0","10.8/11",null,null,284.64100000000002,"9.8 / 9.9","9.8 / 9.9",null,null,188.43700000000001,"10.8 / 11.0","10.8 / 11.0"]
[null,"Cooling DX","East Zone System Efficiency: FEC","EER / IEER","MIN",214.416,null,null,"10.8 / 11.0","10.8 / 11.0",211.05699999999999,null,null,"10.8 / 11.0","10.8 / 11.0",192.791,null,null,"10.8 / 11.0","10.8 / 11.0",189.77699999999999,null,null,"10.8 / 11.0","10.8 / 11.0"]
[]
[null,"Cooling DX","West Zone System Efficiency: ASHRAE","EER / IEER","MIN",269.68700000000001,"9.8 / 9.9","9.8/9.9",null,null,214.91300000000001,"10.8 / 11.0","10.8/11",null,null,282.274,"9.8 / 9.9","9.8 / 9.9",null,null,198.38,"10.8 / 11.0","10.8 / 11.0"]
[null,"Cooling DX","West Zone System Efficiency: FEC","EER / IEER","MIN",205.13900000000001,null,null,"10.8 / 11.0","10.8 / 11.0",222.18,null,null,"10.8 / 11.0","10.8 / 11.0",185.125,null,null,"10.8 / 11.0","10.8 / 11.0",200.19300000000001,null,null,"10.8 / 11.0","10.8 / 11.0"]
[]
[null,"Cooling DX","Core Zone System Efficiency: ASHRAE","EER / IEER","MIN",4146.8530000000001,"9.5 / 9.6","9.5/9.6",null,null,4221.6459999999997,"9.5 / 9.6","9.5/9.6",null,null,3766.172,"9.5 / 9.6","9.5 / 9.6",null,null,3823.4569999999999,"9.5 / 9.6","9.5 / 9.6"]
[null,"Cooling DX","Core Zone System Efficiency: FEC","EER / IEER","MIN",4220.72,null,null,"9.5 / 9.6","9.5 / 9.6",4391.6239999999998,null,null,"9.5 / 9.6","9.5 / 9.6",3705.4160000000002,null,null,"9.5 / 9.6","9.5 / 9.6",3862.5320000000002,null,null,"9.5 / 9.6","9.5 / 9.6"]
[]
[]
[null,null,"Air Economizer (Yes, or No):"]
[null,"Air Economizer","North Zone System Economizer: ASHRAE ","-","-",{"$f":"CoolCapNorthZone","v":233.42},"No","NA",null,null,{"$f":"CoolCapNorthZoneCZ2","v":189.48599999999999},"Yes","NA",null,null,{"$f":"T3CoolCapNorthZone","v":229.11799999999999},"No","NA",null,null,{"$f":"T4CoolCapNorthZone","v":175.67599999999999},"Yes","NA"]
[null,"Air Economizer","North Zone System Economizer: FEC","-","-",{"$f":"CoolCapNorthZoneIECC","v":193.547},null,null,"No","NA",{"$f":"CoolCapNorthZoneIECCCZ2","v":196.292},null,null,"Yes","NA",{"$f":"T3CoolCapNorthZoneIECC","v":173.15299999999999},null,null,"No","NA",{"$f":"T4CoolCapNorthZoneIECC","v":174.999},null,null,"Yes","NA"]
[]
[null,"Air Economizer","South Zone System Economizer: ASHRAE ","-","-",{"$f":"CoolCapSouthZone","v":251.98400000000001},"No","NA",null,null,{"$f":"CoolCapSouthZoneCZ2","v":237.541},"Yes","NA",null,null,{"$f":"T3CoolCapSouthZone","v":253.03},"No","NA",null,null,{"$f":"T4CoolCapSouthZone","v":221.23},"Yes","NA"]
[null,"Air Economizer","South Zone System Economizer: FEC","-","-",{"$f":"CoolCapSouthZoneIECC","v":214.25},null,null,"No","NA",{"$f":"CoolCapSouthZoneIECCCZ2","v":240.49199999999999},null,null,"Yes","NA",{"$f":"T3CoolCapSouthZoneIECC","v":203.761},null,null,"No","NA",{"$f":"T4CoolCapSouthZoneIECC","v":219.21199999999999},null,null,"Yes","NA"]
[]
[null,"Air Economizer","East Zone System Economizer: ASHRAE ","-","-",{"$f":"CoolCapEastZone","v":296.26400000000001},"No","NA",null,null,{"$f":"CoolCapEastZoneCZ2","v":204.035},"Yes","NA",null,null,{"$f":"T3CoolCapEastZone","v":284.64100000000002},"No","NA",null,null,{"$f":"T4CoolCapEastZone","v":188.43700000000001},"Yes","NA"]
[null,"Air Economizer","East Zone System Economizer: FEC","-","-",{"$f":"CoolCapEastZoneIECC","v":214.416},null,null,"No","NA",{"$f":"CoolCapEastZoneIECCCZ2","v":211.05699999999999},null,null,"Yes","NA",{"$f":"T3CoolCapEastZoneIECC","v":192.791},null,null,"No","NA",{"$f":"T4CoolCapEastZoneIECC","v":189.77699999999999},null,null,"Yes","NA"]
[]
[null,"Air Economizer","West Zone System Economizer: ASHRAE ","-","-",{"$f":"CoolCapWestZone","v":269.68700000000001},"No","NA",null,null,{"$f":"CoolCapWestZoneCZ2","v":214.91300000000001},"Yes","NA",null,null,{"$f":"T3CoolCapWestZone","v":282.274},"No","NA",null,null,{"$f":"T4CoolCapWestZone","v":198.38},"Yes","NA"]
[null,"Air Economizer","West Zone System Economizer: FEC","-","-",{"$f":"CoolCapWestZoneIECC","v":205.13900000000001},null,null,"No","NA",{"$f":"CoolCapWestZoneIECCCZ2","v":222.18},null,null,"Yes","NA",{"$f":"T3CoolCapWestZoneIECC","v":185.125},null,null,"No","NA",{"$f":"T4CoolCapWestZoneIECC","v":200.19300000000001},null,null,"Yes","NA"]
[]
[null,"Air Economizer","Core Zone System Economizer: ASHRAE ","-","-",{"$f":"CoolCapCoreZone","v":4146.8530000000001},"No","NA",null,null,{"$f":"CoolCapCoreZoneCZ2","v":4221.6459999999997},"Yes","NA",null,null,{"$f":"T3CoolCapCoreZone","v":3766.172},"No","NA",null,null,{"$f":"T4CoolCapCoreZone","v":3823.4569999999999},"Yes","NA"]
[null,"Air Economizer","Core Zone System Economizer: FEC","-","-",{"$f":"CoolCapCoreZoneIECC","v":4220.72},null,null,"No","NA",{"$f":"CoolCapCoreZoneIECCCZ2","v":4391.6239999999998},null,null,"Yes","NA",{"$f":"T3CoolCapCoreZoneIECC","v":3705.4160000000002},null,null,"No","NA",{"$f":"T4CoolCapCoreZoneIECC","v":3862.5320000000002},null,null,"Yes","NA"]
[]
[]
["Service Water Heating"]
[null,"SWH","SWH Type",null,null,null,"Storage Water Heater",null,"Storage Water Heater",null,null,"Storage Water Heater",null,"Storage Water Heater",null,null,"Storage Water Heater",null,"Storage Water Heater",null,null,"Storage Water Heater",null,"Storage Water Heater"]
[null,"SWH","Fuel Type",null,null,null,"Gas",null,"Gas",null,null,"Gas",null,"Gas",null,null,"Gas",null,"Gas",null,null,"Gas",null,"Gas"]
[null,"SWH","Thermal Efficiency:"]
[null,"SWH","Size <= 75 kBtu/h, Energy Factor (EF)"," - ","MIN",75,0.51800000000000002,0.51800000000000002,0.51800000000000002,0.51800000000000002,77,null,null,null,null,75,0.51800000000000002,0.51800000000000002,0.51800000000000002,0.51800000000000002,77]
[null,"SWH","Size > 75 kBtu/h, Thermal Efficiency (Et)","%","MAX",{"$f":"SWHCapacity","v":75},null,null,null,null,{"$f":"SWHCapacityCZ2","v":77},80,80,80,80,{"$f":"T3SWHCapacity","v":75},null,null,null,null,{"$f":"T4SWHCapacity","v":77},80,80,80,80]