{"text_format":"1","workbook":"xlsx","n_sheets":1,"sheets":["Prototype D7"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":0,"defined_names":36,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Prototype D7","index":0,"n_rows":101,"n_cols":15,"rows_kept":101,"cut":false,"hidden":false,"merged":[[3,5,3,9],[3,10,3,14]]}
[]
["Output Results for Performance Based Code Compliance Reference Design Tests (Envelope Requirements shall use U-Factor for walls and Roofs, and F-Factor for slab-on-grade floors)"]
[]
[null,null,null,null,null,"Test Run 1 (Climate Zone 1)",null,null,null,null,"Test Run 2 (Climate Zone 2)"]
[null,"TYPE","Description of Components","UNITS","MIN / MAX","Sizing Results","Reference Results for Baseline model (ASHRAE)","Compliance Software Baseline Model Results (ASHRAE)","Reference Results for Baseline model (FEC)","Compliance Software Baseline Model Results (FEC)","Sizing Results","Reference Results for Baseline model (ASHRAE)","Compliance Software Baseline Model Results (ASHRAE)","Reference Results for Baseline model (FEC)","Compliance Software Baseline Model Results (FEC)"]
["Envelope Components"]
[null,"Wall","Exterior Wall: U-Value","Btu/(h-ft2-°F)","MAX",null,0.57999999999999996,0.57999999999999996,0.14199999999999999,0.14199999999999999,null,0.151,0.151,0.14199999999999999,0.14199999999999999]
[null,"Wall","Exterior Wall: Thermal Capacity","(Btu/ft2-°F)",null,null,9.02,9.02,"NA","NA",null,9.02,9.02,"NA","NA"]
[null,"Wall","Exterior Wall: Solar Reflectance","-","MIN",null,"NA","NA","NR","NR",null,"NA","NA","NR","NR"]
[null,"Wall","Exterior Wall: Solar Absorptance","-","MAX",null,"NA","NA",0.75,0.75,null,"NA","NA",0.75,0.75]
[null,"Wall","Exterior Wall: Thermal Emittance","-","MIN",null,"NA","NA",0.9,0.9,null,"NA","NA",0.9,0.9]
[null,"Floor","Floor Slab-on-grade: Unheated F-factor","Btu/(h-ft-°F)","MAX",null,0.73,0.73,0.73,0.73,null,0.73,0.73,0.73,0.73]
[null,"Floor","Floor Slab-on-grade: Thermal Capacity","(Btu/ft2-°F)",null,null,9.33,9.33,"NA","NA",null,9.33,9.33,"NA","NA"]
[null,"Roof","Exterior Roof: U-Value","Btu/(h-ft2-°F)","MAX",null,4.8000000000000001E-2,4.8000000000000001E-2,4.8000000000000001E-2,4.8000000000000001E-2,null,4.8000000000000001E-2,4.8000000000000001E-2,4.8000000000000001E-2,4.8000000000000001E-2]
[null,"Roof","Exterior Roof: Thermal Capacity","(Btu/ft2-°F)",null,null,2.7,2.7,"NA","NA",null,2.7,2.7,"NA","NA"]
[null,"Roof","Exterior Roof: Solar Reflectance","-","MIN",null,0.55000000000000004,0.55000000000000004,"NA","NA",null,0.55000000000000004,0.55000000000000004,"NA","NA"]
[null,"Roof","Exterior Roof: Solar Absorptance","-","MAX",null,"NR","NR",0.75,0.75,null,"NR","NR",0.75,0.75]
[null,"Roof","Exterior Roof: Thermal Emittance","-","MIN",null,0.9,0.9,0.9,0.9,null,0.9,0.9,0.9,0.9]
[null,"Floor","Internal Floor: Thermal Capacity","(Btu/ft2-°F)",null,null,9.9,"NC","NA","NA",null,9.9,"NC","NA","NA"]
[null,"Floor","Internal Floor: U-Value","Btu/(h-ft2-°F)","MAX",null,0.33200000000000002,"NC",6.6000000000000003E-2,"NC",null,0.107,"NC",3.3000000000000002E-2,"NC"]
[null,"Fenestration","Exterior Window: U-Value","Btu/(h-ft2-°F)","MAX",null,1.2,1.2,0.65,0.65,null,0.75,0.75,0.65,0.65]
[null,"Fenestration","Exterior Window: SHGC","-","MAX",null,0.25,0.25,0.25,0.25,null,0.25,0.25,0.25,0.25]
[null,"Fenestration","Exterior Window: WWR: Non-Residential","(%)","MAX",null,40,30.6,40,30.6,null,40,30.6,40,30.6]
[null,"Fenestration","Exterior Window: WWR: Residential","(%)","MAX",null,40,17,40,17,null,40,17,40,17]
[null,"Fenestration","Window Area:"]
[null,"Fenestration","Non-Residential"]
[null,"Fenestration","South Window Area","ft2","MAX",null,2310,1704,2310,1704,null,2310,1704,2310,1704]
[null,"Fenestration","East Window Area","ft2","MAX",null,990,804,990,804,null,990,804,990,804]
[null,"Fenestration","North Window Area","ft2","MAX",null,1520.25,1269,1520.25,1269,null,1520.25,1269,1520.25,1269]
[null,"Fenestration","West Window Area","ft2","MAX",null,1386,1023,1386,1023,null,1386,1023,1386,1023]
[null,"Fenestration","Residential"]
[null,"Fenestration","South Window Area","ft2","MAX",null,1728,1726,1728,1726,null,1728,1726,1728,1726]
[null,"Fenestration","East Window Area","ft2","MAX",null,1536,1536,1536,1536,null,1536,1536,1536,1536]
[null,"Fenestration","North Window Area","ft2","MAX",null,1728,1726,1728,1726,null,1728,1726,1728,1726]
[null,"Fenestration","West Window Area","ft2","MAX",null,1536,1536,1536,1536,null,1536,1536,1536,1536]
[null,"Skylight","Skylight Area","ft2","MAX",null,"NA","NA","NA","NA",null,"NA","NA","NA","NA"]
[null,"Skylight","Skylight: U-Value","Btu/(h-ft2-°F)","MAX",null,"NA","NA","NA","NA",null,"NA","NA","NA","NA"]
[null,"Skylight","Skylight: SHGC","-","MAX",null,"NA","NA","NA","NA",null,"NA","NA","NA","NA"]
[null,"Skylight","Skylight: Skylight-Roof Ratio","(%)","MAX",null,"NA","NA","NA","NA",null,"NA","NA","NA","NA"]
[]
["Interior Lighting"]
[null,"Lighting","LPD - Building Area Method: Retail","W/ft2","MAX",null,0.6,0.6,0.7,0.7,null,0.6,0.6,0.7,0.7]
[null,"Lighting","LPD - Building Area Method: Office","W/ft2","MAX",null,0.6,0.6,0.7,0.7,null,0.6,0.6,0.7,0.7]
[null,"Lighting","LPD - Building Area Method: Apartment Units","W/ft2","MAX",null,0.6,0.6,0.7,0.7,null,0.6,0.6,0.7,0.7]
[null,"Lighting","LPD - Building Area Method: Multi-family Hallway","W/ft2","MAX",null,0.6,0.6,0.7,0.7,null,0.6,0.6,0.7,0.7]
[]
["Exterior Lighting",null,null,null,""]
[null,"Lighting","Total Lighting Allowance","W","MAX",null,1450,1450,1450,1450,null,1450,1450,1450,1450]
[]
["Internal Loads"]
[null,"Equipment","Internal Electric Power Density: Retail","W/ft2","-",null,1.5,"NC",1.5,"NC",null,1.5,"NC",1.5,"NC"]
[null,"Equipment","Internal Electric Power Density: Office","W/ft2","-",null,1,"NC",1,"NC",null,1,"NC",1,"NC"]
[null,"Equipment","Internal Electric Power Density: Apartment Units","W/ft2","-",null,1.65,"NC",1.65,"NC",null,1.65,"NC",1.65,"NC"]
[null,"Equipment","Internal Electric Power Density: Multi-family Hallway","W/ft2","-",null,0.7,"NC",0.7,"NC",null,0.7,"NC",0.7,"NC"]
[null,null,null,null,""]
[]
["HVAC System"]
[null,null,"HVAC System Type"]
[null,null,"Retail Floor",null,null,null,"Four-Pipe Fan Coil, Chilled Water, Hot-Water Fossil Fuel Boiler",null,"Four-Pipe Fan Coil, Chilled Water, Hot-Water Fossil Fuel Boiler",null,null,"Four-Pipe Fan Coil, Chilled Water, Hot-Water Fossil Fuel Boiler",null,"Four-Pipe Fan Coil, Chilled Water, Hot-Water Fossil Fuel Boiler"]
[null,null,"Office Floors",null,null,null,"VAV with Reheat, Chilled Water, Hot-Water Fossil Fuel Boiler",null,"VAV with Reheat, Chilled Water, Hot-Water Fossil Fuel Boiler",null,null,"VAV with Reheat, Chilled Water, Hot-Water Fossil Fuel Boiler",null,"VAV with Reheat, Chilled Water, Hot-Water Fossil Fuel Boiler"]
[null,null,"Multi-Family Floors",null,null,null,"Four-Pipe Fan Coil, Chilled Water, Hot-Water Fossil Fuel Boiler",null,"Four-Pipe Fan Coil, Chilled Water, Hot-Water Fossil Fuel Boiler",null,null,"Four-Pipe Fan Coil, Chilled Water, Hot-Water Fossil Fuel Boiler",null,"Four-Pipe Fan Coil, Chilled Water, Hot-Water Fossil Fuel Boiler"]
[]
[]
[null,null,"Boiler Minimum Heating Efficiency:"]
[null,"Oil Boiler","Oil-Fired Boiler Efficiency: ASHRAE","% Et","MIN",710,80,80,null,null,860,80,80]
[null,"Oil Boiler","Oil-Fired Boiler Efficiency: FEC","% Et","MIN",390,null,null,80,80,820,null,null,80,80]
[]
[]
[null,null,"Water Chilling Package Minimum Efficiency:"]
[null,null,"Electrically Operated: "]
[null,null,"Path A: Centrifugal"]
[null,"Chiller","Central Centrifugal Chiller Efficiency: ASHRAE","kW/ton","MIN",265.66000000000003,"0.775 kW/ton, 0.615 IPLV","0.775 kW/ton, 0.615 IPLV",null,null,240.91,"0.775 kW/ton, 0.615 IPLV","0.775 kW/ton, 0.615 IPLV"]
[null,"Chiller","Central Centrifugal Chiller Efficiency: FEC","kW/ton","MIN",253.66,null,null,"0.775 kW/ton, 0.615 IPLV","0.775 kW/ton, 0.615 IPLV",245.83,null,null,"0.775 kW/ton, 0.615 IPLV","0.775 kW/ton, 0.615 IPLV"]
[]
[]
[null,null,"Air Economizer Requirement (Yes, or No):"]
[null,"Air Economizer","Retail North Zone System Economizer: ASHRAE ","-","-",22,"No","NA",null,null,22,"No","NA"]
[null,"Air Economizer","Retail North Zone System Economizer: FEC","-","-",22,null,null,"No","NA",22,null,null,"No","NA"]
[]
[null,"Air Economizer","Retail South Zone System Economizer: ASHRAE ","-","-",24,"No","NA",null,null,24,"No","NA"]
[null,"Air Economizer","Retail South Zone System Economizer: FEC","-","-",24,null,null,"No","NA",24,null,null,"No","NA"]
[]
[null,"Air Economizer","Retail East Zone System Economizer: ASHRAE ","-","-",22,"No","NA",null,null,22,"No","NA"]
[null,"Air Economizer","Retail East Zone System Economizer: FEC","-","-",22,null,null,"No","NA",22,null,null,"No","NA"]
[]
[null,"Air Economizer","Retail West Zone System Economizer: ASHRAE ","-","-",35,"No","NA",null,null,35,"No","NA"]
[null,"Air Economizer","Retail West Zone System Economizer: FEC","-","-",35,null,null,"No","NA",35,null,null,"Yes","NA"]
[]
[null,"Air Economizer","Retail Core Zone System Economizer: ASHRAE ","-","-",26,"No","NA",null,null,26,"No","NA"]
[null,"Air Economizer","Retail Core Zone System Economizer: FEC","-","-",26,null,null,"No","NA",26,null,null,"No","NA"]
[]
[null,"Air Economizer","Office Second Floor System Economizer: ASHRAE ","-","-",300,"No","NA",null,null,300,"Yes","NA"]
[null,"Air Economizer","Office Second Floor System Economizer: FEC","-","-",300,null,null,"No","NA",300,null,null,"Yes","NA"]
[]
[null,"Air Economizer","Office Third Floor System Economizer: ASHRAE ","-","-",360,"No","NA",null,null,360,"Yes","NA"]
[null,"Air Economizer","Office Third Floor System Economizer: FEC","-","-",360,null,null,"No","NA",360,null,null,"Yes","NA"]
[]
[]
["Elevator Motor"]
[null,null,"Electric Motor Power (HP)","HP","MAX",null,20,"NA",20,"NA",null,20,"NA",20,"NA"]
[null,null,"Electric Motor Efficiency (%)","%","MAX",null,92,"NA",92,"NA",null,92,"NA",92,"NA"]