| ELECTRICAL and Swimming Pool Local Technical Amendments to the 2017 6th Edition Florida Building Code |  |  |  |
| --- | --- | --- | --- |
| JURISDICTION | DOCUMENT with TECHNICAL AMENDMENT | TEXT OF TECHNICAL AMENDMENT | TAC REVEW |
| Broward County | Florida Building Code, Building – Ch. 4 – Special Detailed Requirements Based on Use and Occupancy | 454.2.16.1 Electrical. When underwater light fixtures are installed for swimming or bathing pools, these fixtures shall not exceed the following maximum output/ performance standards: 1). 15 volts (RMS) for sinusoidal alternating current 2). 21.2 volts peak for nonsinusoidal alternating current 3). 30 volts continuous direct current 4). 12.4 volts peak for direct current that is interrupted at a rate of 10 to 200 Hertz 5). The maximum incandescent lamp size shall be 300 Watts | Electrical and Swimming Pool TAC |
| Broward County | Florida Building Code, Residential | Amendment to Section E 4206.4.2. E4206.4.2.3 When underwater light fixtures are installed for swimming or bathing pools, these fixtures shall not exceed the following maximum output/ performance standards: 1. 15 volts (RMS) for sinusoidal alternating current 2. 21.2 volts peak for nonsinusoidal alternating current 3. 30 volts continuous direct current 4. 12.4 volts peak for direct current that is interrupted at a rate of 10 to 200 Hertz 5. The maximum incandescent lamp size shall be 300 watts | Electrical and Swimming Pool TAC |
| Pinellas County Construction Licensing Board | Florida Building Code, Building | 2701.1 Scope. This chapter governs the electrical components, equipment and systems used in buildings and structures covered by this code. Electrical components, equipment and systems shall be designed and constructed in accordance with the provisions of the NFPA 70. | Electrical TAC |
| Pinellas County Construction Licensing Board | Florida Building Code, Building | AMEND EXISTING NEC SECTION Article 250.96 Bonding Other Enclosures. (A) General. Metal raceways, cable trays, cable armor, cable sheath, enclosures, frames, fittings, and other metal non-current-carrying parts that are to serve as equipment grounding conductors, with or without the use of supplementary equipment grounding conductors, shall be bonded where necessary to ensure electrical continuity and the capacity to conduct safely any fault current likely to be imposed on them. Any nonconductive paint, enamel, or similar coating shall be removed at threads, contact points, and contact surfaces or be connected by means of fittings designed so as to make such removal unnecessary. All raceways shall contain an equipment-grounding conductor sized in accordance with Table 250.122. | Electrical TAC |
| City of Winter Park | Florida Building Code, Building | 454.3 (Building) and R4501.17.l .16 (Residential) swimming pool enclosure protection during construction. During the construction of public or private swimming pools, the permanent fence or wall meeting all applicable requirements of the Florida Building Code, Residential Volume, Chapter 45, or a temporary fence at least four (4) feet in height above the grade shall be installed. This fence or wall shall be closed, latched and locked at all times, except when work is in progress and workmen are on the site. The temporary fence shall not be removed except when the permanent fence, wall, enclosure or swimming pool is being actively constructed. At no time shall the pool be left by workmen unless secured by either the permanent or temporary enclosure. Swimming pool barrier protection shall allow bodies of water such as lakes, canals and streams to serve as one side of the required barrier when the water frontage is at least six feet wide beyond the shoreline, and the side yard fence barrier proceeds at least one foot into the water body or the fence continues to the edge of the water to the top of a canal or stream bulkhead wall. Provisions in this section l--apply to swimming pools on building sites, including commercial, residential or multifamily projects. Failure to maintain enclosure protection security with a swimming pool protection barrier shall cause the city to secure the pool from outside entry. and authorize the issuance of a "stop work" order until all fees related to providing a pool protection barrier have been paid or waived by the building official minus costs. | Swimming Pool TAC |