| Ann Stanton/DCA/FLEOC 07/06/2006 11:05 AM |  |
| --- | --- |

To

Mo Madani/DCA/FLEOC@fleoc, Betty Stevens/DCA/FLEOC@fleoc, swami@fsec.ucf.edu

cc

Subject

Fw: Glitch cycle version

Comment on code, Mod 1753.

1) The two tables in Mod 1753 for the minimum efficiency for Small-Duct High-Velocity, Air Cooled*  systems contradict each other (11 and 10 SEER). The US Department of Energy has issued exceptions from the SEER 13/HSPF 7.7 rule for three manufacturers' Small-Duct High-Velocity heating and cooling equipment.  Tables 13-407.1.ABC.3.2A, 13-407.1.AB.3.2B, 13-607.1.ABC.3.2A and 13-607.1.ABC.3.2B should be changed to reflect the following values with a footnote 4, that requires a letter of exception from the US Dept. of Energy:

Table 13-407.1.ABC.3.2A [13-607.1.ABC.3.2A]:

Small-Duct High-	<65,000 Btu/h3	All	Split System or 		11.0 SEER4	ARI 210/240

Velocity Air Cooled				Single Package

Table 13-407.1.ABC.3.2B [13-607.1.ABC.3.2B]:

Small-Duct High-	<65,000 Btu/h3	All	Split System or 		11.0 10 SEER4	ARI 210/240

Velocity, Air Cooled,				Single Package

Cooling Mode

4 As granted by U.S. Department of Energy letter of exception, specific to individual companies. SDHV products without a letter of exception shall have the same efficiency as Air-Cooled Air-conditioners.

Please note:  Florida has a very broad public records law.  Most written communications to or from state officials regarding state business are public records available to the public and media upon request.  Your e-mail communications may be subject to public disclosure.