This is an official comment on the 2006 Supplement to the 2004 Florida Energy Code, Building, Chapter 13, Energy Efficiency:

Mod 1782 revised Form 600B-04, updating the three forms for north, central and south Florida to an increased level of stringency resulting from changing the heating and cooling equipment efficiency baselines.  There is a minor change needed to Form 600B to make it more effective:  the "To Be Installed" column on Table 6B-1 needs revision to line it up with changes made to the compliance packages.  The new format for the "To Be Installed" column onTable 6B-1 should read as follows:

FORM 600B  Table 6B-1 [North Florida packages used as example]

| COMPONENT | PACKAGE A | PACKAGE B | PACKAGE C | TO BE INSTALLED |
| --- | --- | --- | --- | --- |
| Glass Overhang U-factor Solar Heat Gain Coefficient | < 18% glass to floor area 2’ overhang required U-factor 0.65 SHGC 0.40 | < 18% glass to floor area 2’ overhang required U-factor 0.65 SHGC 0.65 | < 18% glass to floor area 2’ overhang required Double pane (Default) Clear (Default) | GFA____________ % OH _____________ ft. U-factor:__________ SHGC:____________ |
| Walls (exterior or adjacent) Wood frame CBS Insulation on interior of wall | R-value R-13 R-value R-7 | R-value R-13 R-value R-7 | R-value R-13 R-value R-7 | Exterior Adjacent R= ____ _____ R= ____ _____ |
| Doors | Solid wood or insulated | Solid wood or insulated | Solid wood or insulated |  |
| Ceilings Under attic/single assembly | R-value R-30 | R-value R-38 | R-value R-38 | R=____________ |
| Floor Slab-on-grade Raised floors | R-value R-0 Not allowed | R-value R-0 Not allowed | R-value R-0 Not allowed | R= ____________ Not allowed |
| Cooling system | SEER 13.0 | SEER 13.65 | SEER 15.0 | SEER:_________ |
| Heating system Electric heat pump Gas furnace | HSPF 7.7 AFUE 0.78 (LP gas not allowed) | HSPF 8.1 Nat. gas AFUE 0.78 (LP gas not allowed) | HSPF 8.5 Nat. gas AFUE 0.78 LP gas 0.80 | HSPF:_________ AFUE:_________ AFUE:_________ |
| Water heater Electric water heater Gas water heater Other (see below) | EF 0.94 Nat. gas EF 0.59 (LP gas not allowed) | EF 0.92 Nat. gas EF 0.59 (LP gas not allowed) | EF 0.92 Nat. gas EF 0.59 LP gas 0.63 | EF=___________ EF=___________ EF=___________ |
| Air distribution system Ducts in attic Air handler location | R-value R-6 AHU in the garage or inside conditioned space | R-value R-6 AHU in the garage or inside conditioned space | TESTED (LP gas only) R-value R-6 AHU in the garage or inside conditioned space |  TESTED R = _______________ Location:___________ |