## Commission
92 | 22560 | 0 | New | Ruskin Company | Panel Walls | Wall Louver | Recommend Approval | a
|  |  | M.Steele's comment | FL22560.1 1) I believe the norm is that the test standard “year” as listed on the application is the year as referenced in the FBC. The application lists a year of 2013 for the AMCA 540 test, but the 5th Ed. FBC-Building, Ch. 35, lists the AMCA 540 test standard year as 2008. The application does provide a valid equivalency of standards document for the 540 test. Please change the AMCA 540 test year on the application from “2013” to “2008”. 2) It appears there is a typo in the Model name where it shows two “D”s in EME6625DDFL, where I believe it is supposed to only have one “D”. The supporting documents of Eng. Evaluation Report, Equivalency of Standards, and Installation Instructions all show only one “D” in the model name. Please change the Model name as shown on the application to “EME6625DFL”. 3) Under Limits of Use, Other, the applicant claims an impact level of “E” (enhanced impact level of 80 fps), which is greater than the typical impact level of “D” (Basic impact level of 50 fps). The Evaluation Report (which normally states the exact impact level), Equivalence of Standards report, nor the Installation Instructions do not indicate the higher “E” level of impact resistance. Please have the Validator confirm to the Committee the higher “E” level of impact resistance.
|  |  | T.Berman's response | When an applicant goes through the process of inputting the information on-line on Page 2 the website indicates "Enter the Referenced Standard and Year (of Standard):” As appropriate AMCA 540 and year 2013 were entered. This was the testing standard tested. Next, the screen indicates the following: If Standard and/or Standard Year listed above, is not in the Code, then certify equivalency using one of the following Entities: Listed is: Florida Licensed Licensed Professional Engineer or Architect. An equivalency of standards was certified between AMCA 540-13 and AMCA 540-08 (the adopted standard under 2014 FBC) by a Florida Licensed PE. The equivalency of standards was uploaded on the application. The website instructions clearly indicate that a standard not adopted in the Code could be noted if the proper certificate of equivalency is uploaded. Therefore the application should approved as is.
|  |  | T.Berman's response | We agree with this public comment and request that the application be given a conditional approval based on the following: 2. On the face of the application correct a typo and on the section: Model, Number or Name indicate EME6625DFL. On the second comment about the level impact “E” it is been shown on the face of application and on the installation instructions Page 1 it is also indicated. To clarify as per the comment we request a conditional approval to: 3. On the evaluation report: 5. Supporting Documents: indicate AMCA 540 Level “E" and on 6. Limits and conditions of Use: 3. …….AMCA 540 Level “E” These added indication of the level of impact does not change the performance of the product but indicates in all instances the testing performed.
|  |  | Staff analysis | Staff agrees with the applicant's response and recommends conditional approval to allow the applicant to correct a typo and on the section: Model, Number or Name indicate EME6625DFL and indicate AMCA 540 Level “E" on the evaluation report: item 5. Supporting Documents and on item 6. Limits and conditions of Use: item 3. …….AMCA 540 Level “E”.