Exova Warringtonfire North America		T: 905-822-4111

2395 Speakman Drive		               	F: 905-823-1446

Mississauga, Ontario			  	info@exova.com

Canada					  	www.exova.com

L5K 1B3

ASTM E 84 – Surface Burning Characteristics of Materials

| Test Description: The Steiner Tunnel, designated herein as ASTM E 84, "Standard Method of Test for Surface Burning Characteristics of Building Materials", is designed to determine the relative surface burning characteristics of materials under specific test conditions. Results are expressed in terms of Flame Spread Index (FSI) and Smoke Developed (SD). The tunnel is pre-heated to a specified temperature and allowed to cool to a pre-test temperature. The tunnel lid is raised and the test sample is placed along the ledges of the tunnel so as to form a continuous ceiling 24 feet long, 12 inches above the floor. The lid is then lowered and the ignition burners are ignited at one end of the specimen. The flame spread distance is observed and recorded every 15 seconds and calculations are made to determine FSI and SD, based on comparison data with red oak. |  |  |
| --- | --- | --- |

Sample Requirements: Sample Size: 21 inches (533 mm) x 24 feet (7315 mm) (i.e. 3 pieces, each 21 inches (533 mm) x 8 feet (2438 mm)) Number of Specimens Required: 1 Additional Considerations: Specimen Mounting: If a substrate is required (fiberglass reinforced cement board or gypsum board), then additional sample preparation fees would apply. Specimen Thickness: Specimens thicker than 3 inches (75 mm) require tunnel lid modification. Additional fees would apply.

Application: Steiner Tunnel – Ceiling Mounting American Building Code requirements for building materials, primarily for ceiling and wall material applications Typical Classifications: Class A or 1 (FSI = 0 to 25), Class B or 2 (FSI = 26 to 75), Class C or 3 (FSI = 76 to 200) All classifications specify a maximum Smoke Developed (SD) of 450 Comparable Test Procedures: UL 723, NFPA 255, CAN/ULC-S102, CAN/ULS-S102.2 Accreditation: To ISO/IEC 17025 for a defined Scope of Testing by the International Accreditation Service (IAS)