Preface

Preface, add text after the section, Adoption and Maintenance, to read as follows:

Letter Designations in Front of Section Numbers

In each code development cycle, proposed changes to the code are considered at the Code Development Hearings by the ICC Fire Code Development Committee, whose action constitutes a recommendation to the voting membership for final action on the proposed change. Proposed changes to a code section that has a number beginning with a letter in brackets are considered by a different code development committee. For example, proposed changes to code sections that have [F] in front of them (e.g. [F] 903.1.1.1) are considered by the ICC Fire Code Development Committee at the code development hearings.

The content of sections in this code that begin with a letter designation are maintained by another code development committee in accordance with the following:

[E] = International Energy Conservation Code Development Committee;

[EB] = International Existing Building Code Development Committee;

[EL] = ICC Electrical Code Development Committee;

[F] = International Fire Code Development Committee;

[FG] = International Fuel Gas Code Development Committee;

[M] = International Mechanical Code Development Committee; and

[P] = International Plumbing Code Development Committee.

[Mod 2862]

Chapter 3 General Regulations

Section 305.1 Corrosion revise text to read as follows:

305.1 Corrosion. Pipes passing through concrete or cinder walls and floors or other corrosive material shall be protected against external corrosion by a protective sheathing or wrapping or other means that will withstand any reaction from lime and acid of concrete, cinder or other corrosive material. Sheathing or wrapping shall allow for expansion and contraction of piping to prevent any rubbing action. Minimum wall thickness of material shall be 0.025 0.010 inch (0.64 mm).

Exception: Sleeving is not required for installation of CPVC into concrete or similar material

Section 305.1.2 Penetration, add text to read as follows:

305.1.2 Penetration. Protective sleeves around piping penetrating concrete slab-on-grade floors shall not be of cellulose-containing materials. If soil treatment is used for subterranean termite protection, the sleeve shall have a maximum wall thickness of 0.010 inch, and be sealed within the slab using a non-corrosive clamping device to eliminate the annular space between the pipe and the sleeve. No termiticides shall be applied inside the sleeve.

[Mod 2842]

Section 314.2.3 Auxiliary and secondary drain systems revise text to read as follows:

314.2.3 Auxiliary and secondary drain systems.  No change to text.

1.- 3. [No change]

4. A water level detection device conforming to UL 508 shall be provided that will shut off the equipment served in the event that the primary drain is blocked. The device shall be installed in the primary drain line, the overflow drain line, or in the equipment-supplied drain pan, located at a point higher than the primary drain line connection and below the overflow rim of such pan.

Exception: Fuel-fired appliances that automatically shut down operation in the event of a stoppage in the condensate drainage system.

[Mod 2944rev]

Chapter 4 Fixtures, Faucets and Fixture Settings

Table 403.1 Minimum Number of Required Plumbing Fixtures, revise text to read as follows:

TABLE 403.1

MINIMUM NUMBER OF REQUIRED PLUMBING FIXTURESa

No change to remaining table.

[Mod 3240]

Chapter 5 Water Heaters

Section 502.4 Water heaters installed in attics revise text to read as follows:

502.4 Seismic supports.  Reserved.

502.3 Water heaters installed in attics. Attics containing a water heater shall be provided with an opening and unobstructed passageway large enough to allow removal of the water heater. The passageway shall not be less than 30 inches (762 mm) high and 22 inches (559 mm) wide and not more than 20 feet (6096 mm) in length when measured along the centerline of the passageway from the opening to the water heater. The passageway shall have continuous solid flooring not less than 24 inches (610 mm) wide. A level service space at least 30 inches (762 mm) deep and 30 inches (762 mm) wide shall be present at the front or service side of the water heater. The clear access opening dimensions shall be a minimum of 20 inches by 30 inches (508 mm by 762 mm) where such dimensions are large enough to allow removal of the water heater.

[Mod 3348]

Chapter 6 Water Supply and Distribution

Table 603.1 Minimum Water Service Size, revise text to read as follows:

TABLE 603.1 MINIMUM WATER SERVICE SIZEa

56-5885

[Mod 2829rev]

Section 607.2.1 Circulating systems revise text to read as follows:

607.2.1 Minimum pipe insulation Circulating systems. Circulating hot water piping and domestic and service hot water systems with fluid design operating temperatures greater than 105oF  shall be insulated in accordance with Piping insulation shall conform to the requirements of Table 607.2.1.

Table 607.1 Minimum Pipe Insulation, revise to read as follows:

# TABLE 607.2.1

MINIMUM PIPE INSULATION (in.)a,b

Domestic and Service Hot Water Circulating Systemsa

| Fluid Design Operating Temperature Range (oF) | Insulation Conductivity |  | Nominal Pipe Diameter or Tube Size (inches) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | ConductivityRange Btu in/(h ft2 .oF) | Mean Temperature Rating | <1 | 1-1 ½ | 1 ½ to 4 | 4 to <8 | >8 | Run-outsc Up to 2” | Up to 2” | 1 ½” and up |
| Domestic and Service Hot Water Systemsc |  |  |  |  |  |  |  |  |  |  |
| ≥105 | 0.22 0.24 -0.28 | 100 | 0.5 | 0.5 | 1.0 | 1.0 | 1.0 | 0.5 | 1.0 | 1.5 |

a Section 13-412.AB.3.2.4 of Chapter 13 of the Florida Building Code, Building  requires piping insulation for 1) recirculating system piping, including the supply and return piping of a circulating tank type water heater,  Applies to circulating sections of service or domestic hot water systems, and 2) the first 8’ of outlet piping for a constant temperature nonrecirculating storage system, 3) the inlet pipe between the storage tank and a heat trap in a nonrecirculating storage system and 4)  pipes that are externally heated from storage tank for commercial non-circulating systems. For  residential greater than two-family and less than 4 stories, see Section 13-612.1.ABC.5 of Chapter 13 of the Florida Building Code, Building  requires at least ½ inch insulation for circulating hot water system pipes.

bFor insulation outside the stated conductivity range, the minimum thickness (T) shall be determined as follows: in accordance with Equation 4-2 in 411.1.ABC.2.1 of Chapter 13 of the Florida Building Code, Building.

T=r(1+t/r)K/k - 1

Where T= minimum insulation thickness (in.),

r=actual outside radius of pipe (in.),

t=insulation thickness listed in this table for applicable fluid temperature and pipe size,

K=conductivity of alternate material at mean rating temperature indicated for the applicable fluid temperature (Btu.in.[h.ft2.oF]; and

k=upper value of the conductivity range listed in this table for applicable fluid temperature.

c Piping insulation is not required between the control valve and coil on run-outs when the control valve is located within 4 feet of the coil and the pipe size is 1 inch or less. These thicknesses are based on energy efficiency considerations only.  Additional insulation is sometimes required relative to safety issues/surface temperatures.

cRunouts to individual terminal units not exceeding 12’ in length.

[Mod 2949]

Chapter 7 Sanitary Drainage

Section 701.2 Sewer required revise text to read as follows:

701.2 Sewer required. Every building in which plumbing fixtures are installed and all premises having drainage piping shall be connected to a public sewer, where available, or an approved private sewage disposal system in accordance with Chapter 64E-6, Florida Administrative Code, Standards for Onsite Sewage Treatment and Disposal Systems.

[Mod 3064]

Chapter 10 Traps, Interceptors and Separators

Section 1003.3 Grease interceptors revise text to read as follows:

1003.3 Grease traps and Grease interceptors for public sewer. Grease interceptors shall comply with the requirements of Sections 1003.3.1 through 1003.3.4.2.

1003.3.1 Grease interceptors and automatic grease removal devices required. A grease interceptor or automatic grease removal device shall be required to receive the drainage from fixtures and equipment with grease-laden waste located in food preparation areas, such as in restaurants, hotel kitchens, hospitals, school kitchens, bars, factory cafeterias and clubs. Fixtures and equipment shall include pot sinks, prerinse sinks; soup kettles or similar devices; wok stations; floor drains or sinks into which kettles are drained; automatic hood wash units and dishwashers without prerinse sinks. Grease interceptors and automatic grease removal devices shall receive waste only from fixtures and equipment that allow fats, oils or grease to be discharged.

1003.3.2 Food waste grinders. Where food waste grinders connect to grease interceptors, a solids interceptor shall separate the discharge before connecting to the grease interceptor. Solids interceptors and grease interceptors shall be sized and rated for the discharge of the food waste grinder. Emulsifiers, chemicals, enzymes and bacteria shall not discharge into the food waste grinder.

1003.3.3 Grease interceptors and automatic grease removal devices not required. A grease interceptor or an automatic grease removal device shall not be required for individual dwelling units or any private living quarters.

1003.3.4 Grease interceptors and automatic grease removal devices. Grease interceptors or automatic grease removal devices shall conform to PDI G101, ASME A112.14.3 or ASME A112.14.4 and shall be installed in accordance with the manufacturer’s instructions.

1003.3.4.1 Grease interceptor capacity. Grease interceptors and grease traps shall have the grease retention capacity indicated in Table 1003.3.4.1 for the flow-through rates indicated.

1003.3.4.2 Rate of flow controls. Grease interceptors and grease traps shall be equipped with devices to control the rate of water flow so that the water flow does not exceed the rated flow. The flow-control device shall be vented and terminate not less than 6 inches (152 mm) above the flood rim level or be installed in accordance with the manufacturer’s instructions.

[Mod 3062]

Section 1003.5 Grease interceptors revise text to read as follows:

1003.5 Grease interceptors for onsite sewage treatment and disposal systems. Grease interceptors shall be water and gas tight. Each interceptor shall be engineered to withstand the load, such as from vehicular traffic, to be placed on the interceptor. Sizing of grease interceptors shall be based on the equations of Table 1003.5.1.  The minimum tank volume of grease interceptors shall be 750 gallons (2839 L), and the maximum volume of an individual grease interceptor chamber shall be 1,250 gallons (4731 L). Interceptors shall be permitted to be installed in series or as multi-chambered tanks.

1003.5.1 Grease interceptor capacity. The minimum grease retention capacity for interceptors shall be at least two times the flow-through rate.

1003.5.2 Construction of interceptor. Each interceptor shall be constructed in accordance with Rule 64E-6, Florida Administrative Code. Minimum depth of the liquid shall be 420 inches (106716 mm). Each compartment shall be accessible with a minimum clearance of 18 inches (457 mm) square or in diameter.

1003.5.3 Inlet and outlet piping. The inlet and outlet piping shall have a two-way cleanout tee installed. Inlet piping shall enter at 2½ inches (64 mm) above the liquid level. Inlet piping shall connect to a tee, sweep or baffle, which shall extend to 24 inches (610 mm) below the water level. The outlet pipe shall start at 8 inches (203 mm) above the bottom of the interceptor and extend vertically to a tee. The tee and pipe shall be no less than 4 inches (102 mm) in diameter. The tee shall be installed with the run in the vertical direction.

[Mod 3063 and Mod 3063 Madani comment]

Chapter 13 Reference Standards

Revise text to read as follows:

NFPA 99C—02 05 Gas and Vacuum Systems . . . . . . . . . . . . . . . . . . . . . . . . .  1202.1

[Mod 3246]

APPENDIX C

GRAY WATER RECYCLING SYSTEMS

Section 301.3 Connections to drainage system Revise text to read as follows:

301.3 Connections to drainage system. All plumbing fixtures, drains, appurtenances and appliances used to receive or discharge liquid wastes or sewage shall be directly connected to the sanitary drainage system of the building or premises, in accordance with the requirements of this code. This section shall not be construed to prevent indirect waste systems required by Chapter 8.

Exception: Bathtubs, showers, lavatories, clothes washers and laundry trays shall not be required to discharge to the sanitary drainage system where such fixtures discharge to an approved gray water system for flushing of water closets and urinals or for subsurface landscape irrigation. Any sewage that discharges from the building must be connected to a sanitary drainage system of the building or premises.  The sanitary drainage system shall discharge either to public sewer or to an onsite sewage treatment and disposal system in accordance with the State of Florida Standards for Onsite Sewage Treatment and Disposal Systems.

SECTION C101

GENERAL

Section C101.1 Scope, revise text to read as follows

C101.1 Scope. The provisions of this appendix shall govern the materials, design, construction and installation of gray water systems for flushing of water closets and urinals and for subsurface landscape irrigation (see Figures 1 and 2).

C101.2 Definition. The following term shall have the meaning shown herein.

GRAYWATER. As defined by 381.0065(2)(b) and (d) Florida Statutes, “Graywater” means that part of domestic sewage that is not blackwater, including waste from the bath, lavatory, laundry, and sink, except kitchen sink waste.  “Blackwater” means that part of domestic sewage carried off by toilets, urinals, and kitchen drains Waste discharged from lavatories, bathtubs, showers, clothes washers and laundry trays.

C101.3 Permits. Permits shall be required in accordance with Section 106.

C101.4 Installation. In addition to the provisions of Section C101, systems for flushing of water closets and urinals shall comply with Section C102 and systems for subsurface landscape irrigation shall comply with Section C103. Except as provided for in Appendix C, all systems shall comply with the provisions of the Florida Building Code, Plumbing.

C101.5 Materials. Above-ground drain, waste and vent piping for gray water systems shall conform to one of the standards listed in Table 702.1. Gray water underground building drainage and vent pipe shall conform to one of the standards listed in Table 702.2.

C101.6 Tests. Drain, waste and vent piping for gray water systems shall be tested in accordance with Section 312.

C101.7 Inspections. Gray water systems shall be inspected in accordance with Section 107.

C101.8 Potable water connections. Only connections in accordance with Section C102.3 shall be made between a gray water recycling system and a potable water system.

C101.9 Waste water connections. Gray water recycling systems shall receive only the waste discharge of bathtubs, showers, lavatories, clothes washers or laundry trays.

C101.10 Collection reservoir. Gray water shall be collected in an approved reservoir constructed of durable, nonabsorbent and corrosion-resistant materials. The reservoir shall be a closed and gas-tight vessel. Access openings shall be provided to allow inspection and cleaning of the reservoir interior.

C101.11 Filtration. Gray water entering the reservoir shall pass through an approved filter such as a media, sand or diatomaceous earth filter.

C101.11.1 Required valve. A full-open valve shall be installed downstream of the last fixture connection to the gray water discharge pipe before entering the required filter.

C101.12 Overflow. The collection reservoir shall be equipped with an overflow pipe having the same or larger diameter as the influent pipe for the gray water. The overflow pipe shall be indirectly connected to the sanitary drainage system.

C101.13 Drain. A drain shall be located at the lowest point of the collection reservoir and shall be indirectly connected to the sanitary drainage system. The drain shall be the same diameter as the overflow pipe required in Section C101.12.

C101.14Vent required. The reservoir shall be provided with a vent sized in accordance with Chapter 9 and based on the diameter of the reservoir influent pipe.

SECTION C102

SYSTEMS FOR FLUSHING WATER

CLOSETS AND URINALS

C102.1 Collection reservoir. The holding capacity of the reservoir shall be a minimum of twice the volume of water required to meet the daily flushing requirements of the fixtures supplied with gray water, but not less than 50 gallons (189 L). The reservoir shall be sized to limit the retention time of gray water to a maximum of 72 hours.

C102.2 Disinfection. Gray water shall be disinfected by an approved method that employs one or more disinfectants such as chlorine, iodine or ozone.

C102.3 Makeup water. Potable water shall be supplied as a source of makeup water for the gray water system. The potable water supply shall be protected against backflow in accordance with Section 608. There shall be a full-open valve located on the makeup water supply line to the collection reservoir.

C102.4 Coloring. The gray water shall be dyed blue or green with a food grade vegetable dye before such water is supplied to the fixtures.

C102.5 Materials. Distribution piping shall conform to one of the standards listed in Table 605.4.

C102.6 Identification. Distribution piping and reservoirs shall be identified as containing nonpotable water. Piping identification shall be in accordance with Section 608.8.

Section C103 Subsurface Landscape Irrigation Systems, delete text to read as follows:

SECTION C103

SUBSURFACE LANDSCAPE IRRIGATION SYSTEMS

C103.1 Collection reservoir. Reservoirs shall be sized to limit the retention time of gray water to a maximum of 24 hours.

C103.1.1 Identification. The reservoir shall be identified as containing nonpotable water.

C103.2 Valves required. Acheck valve and a full-open valve located on the discharge side of the check valve shall be installed on the effluent pipe of the collection reservoir.

C103.3 Makeup water. Makeup water shall not be required for subsurface landscape irrigation systems. Where makeup water is provided, the installation shall be in accordance with Section C102.3.

C103.4 Disinfection. Disinfection shall not be required for gray water used for subsurface landscape irrigation systems.

C103.5 Coloring. Gray water used for subsurface landscape irrigation systems shall not be required to be dyed.

C103.6 Estimating gray water discharge. The system shall be sized in accordance with the gallons-per-day-per-occupant number based on the type of fixtures connected to the gray water system. The discharge shall be calculated by the following equation:

C = A _ B

A = Number of occupants:

Residential–Number of occupants shall be determined by the actual number of occupants, but not less than two occupants for one bedroom and one occupant for each additional bedroom.

Commercial–Number of occupants shall be determined by the Florida Building Code, Building.

B = Estimated flow demands for each occupant:

Residential–25 gallons per day (94.6 lpd) per occupant for showers, bathtubs and lavatories and 15 gallons per day (56.7 lpd) per occupant for clothes washers or laundry trays.

Commercial–Based on type of fixture or water use records minus the discharge of fixtures other than those discharging gray water.

C = Estimated gray water discharge based on the total number of occupants.

C103.7 Percolation tests. The permeability of the soil in the proposed absorption system shall be determined by percolation tests or permeability evaluation.

C103.7.1 Percolation tests and procedures. At least three percolation tests in each system area shall be conducted.

The holes shall be spaced uniformly in relation to the bottom depth of the proposed absorption system. More percolation tests shall be made where necessary, depending on system design.

C103.7.1.1 Percolation test hole. The test hole shall be dug or bored. The test hole shall have vertical sides and a horizontal dimension of 4 inches to 8 inches (102 mm to 203 mm). The bottom and sides of the hole shall be scratched with a sharp-pointed instrument to expose the natural soil. All loose material shall be removed from the hole and the bottom shall be covered with 2 inches (51 mm) of gravel or coarse sand.

C103.7.1.2 Test procedure, sandy soils. The hole shall be filled with clear water to a minimum of 12 inches (305 mm)above the bottom of the hole for tests in sandy soils. The time for this amount of water to seep away shall be determined, and this procedure shall be repeated if the water from the second filling of the hole seeps away in 10 minutes or less. The test shall proceed as follows: Water shall be added to a point not more than 6 inches (152 mm) above the gravel or coarse sand. Thereupon, from a fixed reference point, water levels shall be measured at 10-minute intervals for a period of 1 hour. Where 6 inches (152 mm)of water seeps away in less than 10 minutes, a shorter interval between measurements shall be used, but in no case shall the water depth exceed 6 inches (152 mm). Where 6 inches (152 mm) of water seeps away in less than 2 minutes, the test shall be stopped and a rate of less than 3 minutes per inch (7.2 s/mm) shall be reported. The final water level drop shall be used to calculate the percolation rate. Soils not meeting the above requirements shall be tested in accordance with Section C103.7.1.3.

C103.7.1.3 Test procedure, other soils. The hole shall be filled with clear water, and a minimum water depth of 12 inches (305 mm) shall be maintained above the bottom of the hole for a 4-hour period by refilling whenever necessary or by use of an automatic siphon. Water remaining in the hole after 4 hours shall not be removed. Thereafter, the soil shall be allowed to swell not less than 16 hours or more than 30 hours. Immediately after the soil swelling period, the measurements for determining the percolation rate shall be made as follows: Any soil sloughed into the hole shall be removed and the water level shall be adjusted to 6 inches (152 mm) above the gravel or coarse sand. Thereupon, from a fixed reference point, the water level shall be measured at 30-minute intervals for a period of 4 hours, unless two successive water level drops do not vary by more than 11/16 inch (1.59 mm). At least three water level drops shall be observed and recorded. The hole shall be filled with clear water to a point not more than 6 inches (152 mm) above the gravel or coarse sand whenever it becomes nearly empty. Adjustments of the water level shall not be made during the three measurement periods except to the limits of the last measured water level drop. When the first 6 inches (152 mm)of water seeps away in less than 30 minutes, the time interval between measurements shall be 10 minutes and the test run for 1 hour. The water depth shall not exceed 5 inches (127 mm) at any time during the measurement period. The drop that occurs during the final measurement period shall be used in calculating the percolation rate.

C103.7.1.4 Mechanical test equipment. Mechanical percolation test equipment shall be of an approved type.

C103.7.2 Permeability evaluation. Soil shall be evaluated for estimated percolation based on structure and texture in accordance with accepted soil evaluation practices. Borings shall be made in accordance with Section C103.7.1 for evaluating the soil.

C103.8 Subsurface landscape irrigation site location. The surface grade of all soil absorption systems shall be located at a point lower than the surface grade of any water well or reservoir on the same or adjoining property. Where this is not possible, the site shall be located so surface water drainage from the site is not directed toward a well or reservoir. The soil absorption system shall be located with a minimum horizontal distance between various elements as indicated in Table C103.8. Private sewage disposal systems in compacted areas, such as parking lots and driveways, are prohibited. Surface water shall be diverted away from any soil absorption site on the same or neighboring lots.

TABLE C103.8

LOCATION OF GRAY WATER SYSTEM

ELEMENT

MINIMUM HORIZONTAL DISTANCE

HOLDING TANK (feet)

IRRIGATION

DISPOSAL FIELD (feet)

Buildings 5 2

Property line adjoining private property 5 5

Water wells 50 100

Streams and lakes 50 50

Seepage pits 5 5

Septic tanks 0 5

Water service 5 5

Public water main 10 10

For SI: 1 foot = 304.8 mm.

C103.9 Installation. Absorption systems shall be installed in accordance with Sections C103.9.1 through C103.9.5 to provide landscape irrigation without surfacing of gray water.

C103.9.1 Absorption area. The total absorption area required shall be computed from the estimated daily gray water discharge and the design-loading rate based on the percolation rate for the site. The required absorption area equals the estimated gray water discharge divided by the design-loading rate from Table C103.9.1.

TABLE C 103.9.1

DESIGN LOADING RATE PERCOLATION RATE (minutes per inch)

DESIGN LOADING FACTOR (gallons per square foot per day)

0 to less than 10 1.2

10 to less than 30 0.8

30 to less than 45 0.72

45 to 60 0.4

For SI: 1 minute per inch = min/25.4 mm,

1 gallon per square foot = 40.7 L/m2

.

C103.9.2 Seepage trench excavations. Seepage trench excavations shall be a minimum of 1 foot (304 mm) to a maximum of 5 feet (1524 mm) wide. Trench excavations shall be spaced a minimum of 2 feet (610 mm) apart. The soil absorption area of a seepage trench shall be computed by using the bottom of the trench area (width) multiplied by the length of pipe. Individual seepage trenches shall be a maximum of 100 feet (30 480 mm) in developed length.

C103.9.3 Seepage bed excavations. Seepage bed excavations shall be a minimum of 5 feet (1524 mm)wide and have more than one distribution pipe. The absorption area of a seepage bed shall be computed by using the bottom of the trench area. Distribution piping in a seepage bed shall be uniformly spaced a maximum of 5 feet (1524 mm) and a minimum of 3 feet (914 mm)apart, and a maximum of 3 feet (914 mm) and a minimum of 1 foot (305 mm) from the sidewall or headwall.

C103.9.4 Excavation and construction. The bottom of a trench or bed excavation shall be level. Seepage trenches or beds shall not be excavated where the soil is so wet that such material rolled between the hands forms a soil wire. All smeared or compacted soil surfaces in the sidewalls or bottom of seepage trench or bed excavations shall be scarified to the depth of smearing or compaction and the loose material removed. Where rain falls on an open excavation, the soil shall be left until sufficiently dry so a soil wire will not form when soil from the excavation bottom is rolled between the hands. The bottom area shall then be scarified and loose material removed.

C103.9.5 Aggregate and backfill. Aminimum of 6 inches of aggregate ranging in size from ½ to 2½ inches (12.7 mm to 64 mm)shall be laid into the trench below the distribution piping elevation. The aggregate shall be evenly distributed a minimum of 2 inches (51 mm) over the top of the distribution pipe. The aggregate shall be covered with approved synthetic materials or 9 inches (229 mm) of uncompacted marsh hay or straw. Building paper shall not be used to cover the aggregate. A minimum of 9 inches (229 mm) of soil backfill shall be provided above the covering.

C103.10 Distribution piping. Distribution piping shall be not less than 3 inches (76 mm) in diameter. Materials shall comply with Table C103.10. The top of the distribution pipe shall be not less than 8 inches (203 mm)below the original surface. The slope of the distribution pipes shall be a minimum of 2 inches (51 mm)and a maximumof 4 inches (102 mm)per 100 feet (30 480 mm).

TABLE C103.10

DISTRIBUTION PIPE MATERIAL STANDARD

Polyethylene (PE) plastic pipe ASTM F 405

Polyvinyl chloride (PVC) plastic pipe ASTM D 2729

Polyvinyl chloride (PVC) plastic pipe with pipe stiffness of PS 35 and PS 50 ASTM F 1488

C103.11 Joints. Joints in distribution pipe shall be made in accordance with Section 705 of this code.

Delete figure 1 and rename figure 2 as figure 1

[Mod 3060]