Note:  throughout the document wherever the following documents are used, they shall be replaced with Florida specific references: change International Building Code to Florida Building Code, Building; change the ICC Electrical Code to Chapter 27 of the Florida Building Code, Building; change the International Energy Conservation Code to Chapter 13 of the Florida Building Code, Building; change the International Existing Building Code to Florida Building Code, Existing Building; change the International Fire code to Florida Fire Prevention Code; change International Fuel Gas Code to Florida Building Code, Fuel Gas; change the International Mechanical Code to Florida Building Code, Mechanical; change the International Plumbing Code to Florida Building Code, Plumbing; change the International Residential Code to Florida Building Code, Residential.

Chapter 1, Administration

101.1 Scope.  Change to read as shown.

101.1 Scope.  The provisions of Chapter 1, Florida Building Code, Building shall govern the administration and enforcement of the Florida Building Code, Fuel Gas.

101.2 Scope.  Change to read as shown.

101.2 Scope.  Reserved.

101.3 Appendices.  Change to read as shown.

101.3 Appendices.  Reserved.

101.4 Intent.  Change to read as shown.

101.4 Intent.  Reserved.

101.5 Severability.  Change to read as shown.

101.5 Severability.  Reserved.

Section 102 Applicability.  Change to read as shown.

Section 102 Applicability.  Reserved.

Section 103 Department of Inspection.  Change to read as shown.

Section 103 Department of Inspection.  Reserved.

Section 104 Duties and Powers of the Code Official.  Change to read as shown.

Section 104 Duties and Powers of the Code Official.  Reserved.

Section 105 Approval.  Change to read as shown.

Section 105 Approval.  Reserved.

Section 106 Permits.  Change to read as shown.

Section 106 Permits.  Reserved.

Section 107 Inspections and Testing.  Change to read as shown.

Section 107 Inspections and Testing.  Reserved.

Section 108 Violations.  Change to read as shown.

Section 108 Violations.  Reserved.

Section 109 Means of Appeal.  Change to read as shown.

Section 109 Means of Appeal.  Reserved.

Section 110 Temporary Equipment, Systems and Uses.

Section 110 Temporary Equipment, Systems and Uses.  Reserved.

Chapter 2, Definitions

201.4 Terms not defined.  Change to read as shown.

201.4 Terms not defined.  Where terms are not defined through the methods authorized by this section, such terms shall have the meanings as defined in Webster’s Third New International Dictionary of the English Language Unabridged.

202 General Definitions.  Change to read as shown.

REGULATOR. A device for controlling and maintaining a uniform gas supply pressure, either pounds to pounds, pounds-to-inches water column or inches-to-inches water column (appliance regulator).

RISER, GAS.  A vertical pipe supplying fuel gas to a meter assembly or a pressure regulator.

UTILITY GASES. Natural gas, manufactured gas, liquefied petroleum gas-air mixture or mixtures of any of these gases.

Chapter 3, General Regulations.

301.1 Scope.  Change to read as shown.

301.1 Scope. This chapter shall govern the approval and installation of all equipment and appliances that comprise parts of the installations regulated by this code in accordance with Section 301.1.1.

301.1.1 Scope.  Change to read as shown.

301.1.1 This code shall apply to the installation of fuel gas piping systems, fuel gas utilization equipment, and related accessories as follows:

1. Coverage of piping systems shall extend from the point of delivery to the connections with gas utilization equipment (see “Point of delivery”).

2 .Systems with an operating pressure of 125 psig (862 kPa gauge) or less.

Piping systems for gas-air mixtures within the flammable range with an operating pressure of 10 psig (69 kPa gauge).

LP-gas piping systems with an operating pressure of 20 psig (140 kPa) or less.

3. Piping systems requirements shall include design, materials, components, fabrication, assembly, installation, testing, inspection, operation and maintenance.

4. Requirements for gas utilization equipment and related accessories shall include installation, combustion and ventilation air and venting.

This code shall not apply to the following:

1. Portable LP-gas equipment of all types that are not connected to a fixed fuel piping system.

2. Installation of farm equipment such as brooders, dehydrators, dryers and irrigation equipment.

3. Raw material (feedstock) applications except for piping to special atmosphere generators.

4. Oxygen-fuel gas cutting and welding systems.

5. Industrial gas applications using gases such as acetylene and acetylenic compounds, hydrogen, ammonia, carbon monoxide, oxygen and nitrogen.

6. Petroleum refineries, pipeline compressor or pumping stations, loading terminals, compounding plants, refinery tank farms and natural gas processing plants.

7. Integrated chemical plants or portions of such plants where flammable or combustible liquids or gases are produced by chemical reactions or used in chemical reactions.

8. LP-gas installations at utility gas plants.

9. Liquefied natural gas (LNG) installations.

10. Fuel gas piping in power and atomic energy plants.

11. Proprietary items of equipment, apparatus, or instruments such as gas generating sets, compressors and calorimeters.

12.LP-gas equipment for vaporization, gas mixing and gas manufacturing.

13. Temporary LP-gas piping for buildings under construction or renovation that is not to become part of the permanent piping system.

14. Installation of LP-gas systems for railroad switch heating.

15. Installation of LP-gas and compressed natural gas (CNG) systems on vehicles.

16. Gas piping, meters, gas pressure regulators, and other appurtenances used by the serving gas supplier in the distribution of gas, other than undiluted LP-gas.

17. Building design and construction, except as specified herein.

Overlap with Florida Specific – Plumbing TAC

305.4 Public garages.  Change to read as shown.

FBC

305.4 Public garages/parking  structures.  Appliances shall be installed in accordance with the manufacturer’s instructions and NFPA 88B.

IFGC ’09 is changed. Resolve potential conflicts:

305.4 Public garages. Appliances located in public garages, motor fuel-dispensing facilities, repair garages or other areas frequented by motor vehicles shall be installed a minimum of 8 feet (2438 mm) above the floor. Where motor vehicles exceed 6 feet in height and are capable of passing under an appliance, appliances shall be installed a minimum of 2 feet higher above the floor than the height of the tallest vehicle the appliance shall be installed at the clearances required by the appliance manufacturer and not less than 1 foot (305 mm) higher than the tallest vehicle garage door opening.

Exception: The requirements of this section shall not apply where the appliances are protected from motor vehicle impact and installed in accordance with Section 305.3 and NFPA 30A.

Staff recommendation:  should retain Florida Specific provisions.  Recommend keeping Florida Specific provisions since changes in text from the 2009 IFGC do not cover Florida specific requirements limiting installation of appliances in public garages/parking structures to manufacturer’s installation instructions and NFPA 88B.

305.5 Private garages.  Change to read as shown.

305.5 Private garages. Reserved

Overlap with Florida Specific – Plumbing TAC

Section 306.3 Appliances in attics.  Change to read as shown.

FBC

306.3 Appliances in attics. Attics containing appliances requiring access shall be provided with an opening and unobstructed passageway large enough to allow removal of the largest component of the appliance.  The passageway shall not be less than 30 inches (762 mm) high and 22 inches (559 mm) wide and not more than 6 feet (1829 mm in length when measured along the centerline of the passageway from the attic access opening to the appliance’s service panel. The passageway shall have continuous solid flooring not less than 24 inches (610 mm) wide. A level service space not less than 30 inches (762 mm) deep and 30 inches (762 mm) wide shall be

present at the front or service side of the appliance. The clear access opening dimensions shall be a minimum of 20 inches by 30 inches (508 mm by 762 mm), where such dimensions are large enough to allow removal of the largest component of the appliance.

Exception:

The passageway and level service space are not required where the appliance is capable of being serviced and removed through the required opening.

IFGC ’09 is changed as shown. Resolve potential conflicts. Be consistent with the FBC-Mechanical.

[M] 306.3 Appliances in attics. Attics containing appliances shall be provided with an opening and unobstructed passageway large enough to allow removal of the largest component of the appliance. The passageway shall not be less than 30 inches (762 mm) high and 22 inches (559 mm) wide and not more than 20 feet (6096 mm)in length when measured along the centerline of the passageway from the opening to the appliance equipment. The passageway shall have continuous solid flooring not less than 24 inches (610 mm) wide. A level service space not less than 30 inches (762 mm) deep and 30 inches (762 mm) wide shall be present at the front or service side of the appliance equipment.. The clear access opening dimensions shall be a minimum of 20 inches by 30 inches (508 mm by 762 mm), where such dimensions are and large enough to allow removal of the largest component of the appliance.

Exceptions:

1. The passageway and level service space are not required where the appliance is capable of being serviced and removed through the required opening.

2. Where the passageway is not less than 6 feet (1829  mm) high for its entire length, the passageway shall be not greater than 50 feet (15 250 mm) in length.

Staff recommendation:  should retain Florida Specific provisions.  Recommend using the 2009 IFGC language as the base text and add to it Florida specific provisions limiting passageway length to 6 feet.

Overlap with Florida Specific – Plumbing TAC

Change Section 306.3.1 as shown:

FBC

306.3.1 Electrical requirements. A lighting fixture with receptacle outlet, controlled by a switch located at the required passageway opening, shall be provided so as to light the passageway and service area and installed in accordance with Chapter 27 of the Florida Building Code, Building

IFGC ’09 is changed as shown. Resolve potential conflicts. Correlate with FBC-Mechanical.

[M] 306.3.1 Electrical requirements. A luminaire controlled by a switch located at the required passageway opening and a receptacle outlet shall be provided at or near the appliance location in accordance with NFPA 70.

Staff recommendation:  should retain Florida Specific provisions.  Recommend keeping Florida Specific provisions since changes in text from the 2009 IFGC do not cover Florida specific requirements mandating receptacle outlet and lighting for the passageway and service area.

306.3.2  Add to read as shown:

306.3.2 Air-handling units. Air-handling units shall be allowed in residential attics if the following conditions are met:

1. The service panel of the equipment is located within 6 feet (1829 mm) feet of an attic access.

2. A device is installed to alert the owner or shut the unit down when the condensation drain is not working properly.

3. The attic access opening is of sufficient size to replace the air handler.

4. A notice is posted on the electric service panel indicating to the homeowner that the air handler is located in the attic. Said notice shall be in all capitals, in 16-point type, with the title and first paragraph in bold:

NOTICE TO HOMEOWNER

A PART OF YOUR AIR-CONDITIONING SYSTEM, THE AIR HANDLER, IS LOCATED IN THE ATTIC. FOR PROPER, EFFICIENT, AND ECONOMIC OPERATION OF THE AIR-CONDITIONING SYSTEM, YOU MUST ENSURE THAT REGULAR MAINTENANCE IS PERFORMED.  YOUR AIR-CONDITIONING SYSTEM IS EQUIPPED WITH ONE OR BOTH OF THE FOLLOWING:  1) A DEVICE THAT WILL ALERT YOU WHEN THE CONDENSATION DRAIN IS NOT WORKING PROPERLY, OR 2) A DEVICE THAT WILL SHUT THE SYSTEM DOWN WHEN THE CONDENSATION DRAIN IS NOT WORKING. TO LIMIT POTENTIAL DAMAGE TO YOUR HOME, AND TO AVOID DISRUPTION OF SERVICE, IT IS RECOMMENDED THAT YOU ENSURE PROPER WORKING ORDER OF THESE DEVICES BEFORE EACH SEASON OF PEAK OPERATION.

309.1 Grounding.  Change to read as shown.

309.1 Grounding. Each above-ground portion of a gas piping system upstream from the equipment shutoff valve shall be electrically continuous and bonded to any grounding electrode, as defined by Chapter 27 of the Florida Building Code, Building.

Section 311  Add text to read as follows:

SECTION 311

CARBON MONOXIDE CONTROL SYSTEMS

311 Carbon monoxide control systems.  See Section 913 of the Florida Building Code, Building.

Chapter 4 Gas Piping Installations

401.2 Liquefied petroleum gas storage.  Change to read as shown.

401.2 Liquefied petroleum gas storage. The storage system (container, regulators, piping and all components upstream to the point of delivery) for liquefied petroleum gas shall be designed and installed in accordance with the Florida Fire Prevention Code and NFPA 58.

404.15.3 Tracer.  Change to read as shown.

404.15.3 Tracer.  An insulated copper tracer wire or other approved conductor shall be installed adjacent to underground nonmetallic gas piping. Access shall be provided to the tracer wire or the tracer wire shall terminate above ground at each end of the nonmetallic gas piping. The tracer wire size shall not be less than 18 AWG and the insulation type shall be suitable for direct burial.

406.7.4 Placing appliances and equipment in operation.  Change to read as shown.

406.7.4 Placing equipment in operation.  After the piping has been placed in operation, all equipment shall be placed in operation per its listing and the manufacturer’s instructions.

Section 411.1.7 Add section [in ’07 FBC-FG was 411.1.5], Outdoor appliance connectors, to read as shown:

411.1.7 Outdoor appliance connectors. Outdoor gas hose connectors are permitted to connect portable outdoor gas-fired equipment. An equipment shutoff valve, a listed quick-disconnect device, or a listed gas convenience outlet shall be installed where the connector is attached to the supply piping and in such a manner as to prevent the accumulation of foreign matter. Lengths shall not exceed 12 feet (3658 mm) and the connection shall only be made in the outdoor area where the equipment is to be used.

Chapter 5, Chimneys & Vents

503.8 Venting system termination location.  Change to read as shown.

503.8 Venting system termination location.  The location of venting system terminations shall comply with the following (see Appendix C):

[1. – 4. No change]

Chapter 6, Specific Appliances

Section 615.  Sauna Heaters.  Change to read as shown.

Section 615.  Sauna Heaters Reserved

Chapter 8 Referenced Standards

Referenced Standards.  Change to read as shown.

Florida Codes     Florida Building Commission

c/o Florida Department of Community Affairs

Building Codes and Standards

2555 Shumard Oak Boulevard

Tallahassee, FL 32399-2100

Standard                                                                                                              Referenced in code

reference number    Title                                                                                           section number

FBC-B—10           Florida Building Code, Building		       101.1, 201.3, 301.14, 302.1, 302.2, 305.6, 306.6,

401.1.1, 412.6, 413.3, 413.3.1, 501.1, 501.3, 501.12, 501.15.4, 609.3, 614.2, 706.1, 706.3

Chapter 13              Florida Building Code, Building:  Energy Efficiency                                                              301.2

Chapter 27             Florida Building Code, Building:  Electrical (NEC/NFPA 70)		      201.3, 306.3.1,

306.4.1, 306.5.2, 309.1, 309.2, 413.8.2.4, 703.6, 706.3.6,

FBC-M—10          Florida Building Code, Mechanical	       201.3, 301.10, 301.13, 304.11, 501.1, 614.2,

618.5, 621.1,  624.1, 631.2, 632.1, 703.1.2, 706.3.2

FBC-P—10           Florida Building Code, Plumbing	                                                      201.3, 301.6,  624.1.1, 624.2

FRC—10               Florida Residential Code	                                                                                                       703.2.1

FFPC—10             Florida Fire Prevention Code	   201.3, 303.4, 401.2, 412.1, 412.6, 412.7, 412.7.3, 412.8,

413.1, 413.3, 413.3.1, 413.4, 413.8.2.5, 701.1, 701.2, 703.2, 703.2.2, 703.3.8, 703.4,

703.5, 704.1.2, 704.3, 704.4, 706.2, 706.3.4, 706.3.5, 707.1, 707.2, 708.1

UL           Underwriters Laboratories, Inc.

333 Pfingsten Road

Northbrook, IL 60062

Standard                                                                                                             Referenced in code

reference number    Title                                                                                          section number

795—01            Commercial-Industrial Gas Heating Equipment 	                                        610.1, 618.1, 631.1

[IPC ’09 references UL 795-06]