Florida Supplement to the 2009 IRC

PREFACE. Change to read as shown:

The base codes for the 2010 edition of the Florida Building Code include: the International Building Code, 2009 edition; the International Plumbing Code, 2009 edition; the International Mechanical Code, 2009 edition; the International Fuel Gas Code, 2009 edition, the International Energy Efficiency Code, 2009 edition,  the International Residential Code, 2009 edition; the International Existing Building Code, 2009 edition; the National Electrical Code, 2008 edition; the U.S. Department of Housing and Urban Development’s Fair Housing Guidelines and; substantive criteria from the American Society of Heating, Refrigerating and Air-conditioning Engineers’ (ASHRAE) Standard 90.1-2001.  State and local codes adopted and incorporated in the Code include the Florida Energy Efficiency Code for Building Construction, the Florida Accessibility Code for Building Construction and special hurricane protection standards for the High Velocity Hurricane Zone.

Add to read as shown.

Note:  throughout the document, change International Building Code to Florida Building Code, Building; change the ICC Electrical Code to Chapter 27 of the Florida Building Code, Building; change the International Energy Conservation Code to Chapter 13 of the Florida Building Code, Building; change the International Existing Building Code to Florida Building Code, Existing Building; change the International Fire code to Florida Fire Prevention Code; change International Fuel Gas Code to Florida Building Code, Fuel Gas; change the International Mechanical Code to Florida Building Code, Mechanical; change the International Plumbing Code to Florida Building Code, Plumbing; change the International Residential Code to Florida Building Code, Residential.

CHAPTER 1:  ADMINISTRATION

R101.1  Change to read as shown:

R101.1 Title. These provisions shall be known as the Florida Building Code, Residential, and shall be cited as such and will be referred to herein as “this code.”

R101.2  Change to read as shown:

R101.2 Scope. The provisions of the Florida Building Code, Residential, shall apply to the construction, alteration, movement, enlargement, replacement, repair, equipment, use and occupancy, location, removal and demolition of detached one– and two–family dwellings and multiple single–family dwellings (townhouses) not more than three stories above grade plane in height with a separate means of egress and their accessory structures.

Exceptions:

1. Live/work units complying with the requirements of Section 419 of the Florida Building Code, Building  shall be permitted to be built as one- and two-family dwellings or townhouses. Fire suppression required by Section 419.5 of the Florida  Building Code, Building when constructed under the Florida Building Code, Residential  shall conform to Section 903.3.1.3 of the International Building Code.

2. Existing buildings undergoing repair, alteration or additions, and change of occupancy shall comply with the Florida Existing Building Code.

R101.2.1 The provisions of Chapter 1, Florida Building Code, Building, shall govern the administration and enforcement of the Florida Building Code, Residential.

R101.3 Intent.  Change to read as shown.

R101.3 Intent.  Reserved.

R102 through R114 Change to read as shown:

Sections R102 through R114, [use title for each section]  Reserved.

CHAPTER 2:  DEFINITIONS

R201.3  Terms defined in other codes. Change to read as shown:

R201.3 Terms defined in other codes. Where terms are not defined in this code such terms shall have meanings ascribed to them as in other code publications of the Florida Building Commission.

R201.4  Terms not defined. Change to read as shown:

R201.4 Terms not defined.  Where terms are not defined through the methods authorized by this section, such terms shall have the meanings as defined in Webster’s Third New International Dictionary of the English Language Unabridged.

Section R201.5 is added to read as follows:

R201.5  Terms relevant to the energy provisions of Chapter 11 shall be as defined in Section N1100.7.3.

R202  DEFINITIONS.  Change the following definition to read as shown:

ACCESSIBLE. Having access to but which first may require the removal of a panel, door or similar covering of the item described (see Readily Accessible)

Section R202, Definitions.  Add the following definitions:

APPLICABLE GOVERNING BODY. A city, county, state, state agency or other political government subdivision or entity authorized to administer and enforce the provisions of this code, as adopted or amended. Also applies to administrative authority.

ARCHITECT.  A Florida-registered architect.

AWNING: Any rigid or movable (retractable) roof-like structure, cantilevered, or otherwise entirely supported from a building.  An awning is comprised of a lightweight rigid or removable skeleton structure over which an approved cover is attached.

BALLOON-FRAME CONSTRUCTION. A method of construction where the studs are continuous from floor to floor to the roof of the structure.

Section R202, Definitions.  Revise the following definitions:

BASIC WIND SPEED. Three-second gust speed at 33 feet (10,058 MM) above the ground as given in Figure R301.2(4).

Overlap with Florida Specific – Structural TAC

FBC

BRACED WALL LINE. A series of braced wall panels in a single story constructed in accordance with Section R602.2.10 for wood framing or Section R603.7 for cold-formed steel framing to resist racking from wind forces.

IRC ’09 definition is changed. Resolve potential conflicts.

BRACEDWALL LINE. A straight line through the building plan that represents the location of the lateral resistance provided by the wall bracing.

BRACED WALL LINE, CONTINUOUSLY SHEATHED. A braced wall line with structural sheathing applied to all sheathable surfaces including the areas above and below openings.

Staff recommendation:  Florida Specific requirements are covered by the I – Code language.  Recommend using IRC09 definitions instead.

BRACED WALL PANEL. A full-height section of wall constructed to resist in-plane shear loads through interaction of framing members, sheathing material and anchors. The panel’s length meets the requirements of its particular bracing method, and contributes toward the total amount of bracing required along its braced wall line in accordance with Section R602.2.10.1.

Section R202, Definitions.  Add the following definitions:

CANOPY: Any fixed roof-like structure, not movable like an awning, and which is cantilevered in whole or in part self-supporting, but having no side walls or curtains other than valances not more than 18 inches (457 mm) deep.  Lean-to canopies, fixed umbrellas and similar structures are included in this classification. Structures having side walls or valances more than 18 inches (457 mm) deep shall be classified as a tent as set forth herein.

CARBON MONOXIDE ALARM. A device for the purpose of detecting carbon monoxide, that produces a distinct audible alarm, and is listed or labeled with the appropriate standard, either ANSI/UL 2034 - 96, Standard for Single and Multiple Station CO Alarms, or UL 2075 - 04, Gas and Vapor Detector Sensor, in accordance with its application.

CIRCULAR STAIRS. A stairway with steps that result in a sweeping circular or curved pattern, but not spiral stairs.

COMMISSION. Means the Florida Building Commission created by this part.

Section R202, Definitions.  Revise the following definition:

CONDITIONED SPACE. For energy purposes: See Space (a) conditioned space, Chapter 11, Section N1100.7.3. For mechanical purposes, an area, room or space being heated or cooled by any equipment or appliance.

Section R202, Definitions.  Add the following definitions:

DECORATIVE CEMENTITIOUS COATING. A skim coat, as defined in ASTM C 926, of Portland cement-based plaster applied to concrete or masonry surfaces intended for cosmetic purposes.

ENGINEER. A Florida-registered engineer.

ENFORCEMENT AGENCY.

Local enforcement agency. Means an agency of local government with authority to make inspections of buildings and to enforce the codes which establish standards for design, construction, erection, alteration, repair, modification or demolition of public or private buildings, structures or facilities.

State enforcement agency. Means the agency of state government with authority to make inspections of buildings and to enforce the codes, as required by this part, which establish standards for design, construction, erection, alteration, repair, modification or demolition of public or private buildings, structures or facilities.

FABRIC COVERED FRAMEWORK (FCF): A non-pressurized structure which is composed of a rigid framework to support tensioned membrane or fabric which provides the weather barrier.

Section R202, Definitions.  Revise the following definition:

FIRE SEPARATION DISTANCE. The distance measured from the building face to one of the following:

1. To the closest interior lot line; or

2. To the centerline of a street, an alley, easement or public way; or

3. To an imaginary line between two buildings on the lot.

The distance shall be measured at a right angle from the face of the wall.

FOAM PLASTIC INTERIOR TRIM. Foam plastic used as picture molds, chair rails, baseboards, handrails, ceiling beams, door trim and window trim and meeting the requirements of Section R314.6.

Section R202, Definitions.  Add the following definitions:

FOSSIL FUEL. Coal, kerosene, oil, fuel gases, or other petroleum or hydrocarbon product that emits carbon monoxide as a by-product of combustion.

FRAMEWORK. A skeletal or structural frame; an openwork frame structure.

GARAGE DOOR MANUFACTURER.  The party responsible for the completed assembly of the garage door components.

Section R202, Definitions.  Change to read as shown.

HABITABLE SPACE.  A space in a structure for living, sleeping, eating or cooking.  Bathrooms, toilet compartments, closets, halls, screen enclosures, sunroom Categories I, II and III as defined in the AAMA/NPEA/NSA 2100, storage or utility space and similar areas are not considered habitable spaces.

Section R202, Definitions.  Add the following definitions:

HEATING. See Chapter 28 of the Florida Building Code, Building and the Florida Building Code, Mechanical.

HIGH VELOCITY HURRICANE ZONE (HVHZ). This zone consists of Broward and Dade counties.

LANDSCAPE ARCHITECT. A Florida registered Landscape Architect.

Section R202, Definitions.  Change to read as shown.

LIVE LOADS. Those loads produced by the use and occupancy of the building or other structure and do not include construction or environmental loads such as wind load, snow load rain load, earthquake load, flood load or dead load.

MANUFACTURED HOME (Mobile Home). Any residential unit, constructed to standards promulgated by the United States Department of Housing and Urban Development (HUD), away from the installation site, and which bears the HUD label.

Section R202, Definitions.  Add the following definitions:

MATERIAL CODE VIOLATION. A material code violation is a violation that exists within a completed building, structure or facility which may reasonably result, or has resulted, in physical harm to a person or significant damage to the performance of a building or its systems.

MATERIAL VIOLATION. As defined in Florida Statutes.

MEANS OF ESCAPE. A way out of a building or structure that does not conform to the strict definition of means of egress but does provide an alternate way out. A means of escape consists of a door, stairway, passage or hall providing a way of unobstructed travel to the outside at street or ground level that is independent of and remotely located from the means of egress. It may also consist of a passage through an adjacent nonlockable space, independent of and remotely located from the means of egress, to any approved exit.

MODULAR HOME. Any residential unit, constructed to standards promulgated by the Florida Building Commission, away from the installation site, and which bears a Department of Community Affairs Insignia.

Section R202, Definitions.  Change to read as shown.

Overlap with Florida Specific – Structural TAC

FBC

NATURALLY DURABLE WOOD.  The heartwood of the following species with the exception that an occasional piece with corner sapwood is permitted if 90 percent or more of the width of each side on which it occurs is heartwood:

- Decay resistant – Redwood, cedar, black locust and black walnut.

- Termite resistant – Redwood and Eastern red cedar.

IRC ’09 is changed as shown. Resolve potential conflicts.

NATURALLY DURABLE WOOD. The heartwood of the following species with the exception that an occasional piece with corner sapwood is permitted if 90 percent or more of the width of each side on which it occurs is heartwood.

Decay resistant. Redwood, cedar, black locust and black walnut.

Termite resistant. Alaska yellow cedar, redwood, Eastern red cedar and Western red cedar including all sapwood of Western red cedar.

Staff recommendation:  Florida Specific requirements are covered by the IRC09 language.  Recommend using the IRC09 definition instead.

Section R202, Definitions.  Add the following definitions:

OPENINGS.  Apertures or holes in the building envelope which allow air to flow through the building envelope and which are designed as “open” during design winds as defined by these provision.

PERMANENT LABEL.  A label that cannot be removed without noticeable damage.

PLANS. All construction drawings and specifications for any structure necessary for the building official to review in order to determine whether a proposed structure, addition or renovation will meet the requirements of this code and other applicable codes.

REGISTERED TERMITICIDE. Product listed as registered for use as a preventative treatment for termites for new construction by the Florida Department of Agriculture and Consumer Services under authority of Chapter 487, Florida Statutes.

RESIDENT SLEEPING UNIT. A single unit providing sleeping facilities for one or more persons. Resident sleeping units can also include permanent provisions for living, eating and sanitation, but do not include kitchen facilities.

RETAINING WALL, SEGMENTAL. A retaining wall formed of modular block units stacked dry without mortar.

SCREEN ENCLOSURE. A building or part thereof, in whole or in part self-supporting, and having walls of insect screening with or without removable vinyl or acrylic wind break panels and a roof of insect screening, plastic, aluminum or similar lightweight material.

Section R202, Definitions.  Change to read as shown.

SEISMIC DESIGN CATEGORY.  Reserved.

Section R202, Definitions.  Add the following definitions:

SEPARATE ATMOSPHERE.  The atmosphere that exists between rooms, spaces or areas that are separated by an approved smoke barrier.

Section R202, Definitions.  Change to read as shown.

SHEAR WALL. A general term for walls that are designed and constructed to resist racking from seismic and wind by use of masonry, concrete, cold-formed steel or wood framing in accordance with Chapter 6 of this code and the associated limitations in Section R301.2 of this code.

Section R202, Definitions.  Add the following definitions:

SPIRAL STAIRS. A stairway with steps that have a central connecting point, and the travel path is a corkscrew or spiral.

STREET. Any public thoroughfare, street, avenue, boulevard or space more than 20 ft (6096 mm) wide which has been dedicated or deeded for vehicular use by the public and which can be used for access by fire department vehicles.

Section R202, Definitions.  Change to read as shown.

SUNROOM.

- A room with roof panels that include sloped glazing that is a one-story structure added to an existing dwelling with an open or glazed area in excess of 40 percent of the gross area of the sunroom structure’s exterior walls and roof.

- A one-story structure added to a dwelling with structural roof panels without sloped glazing. The sunroom walls may have any configuration, provided the open area of the longer wall and one additional wall is equal to at least 65 percent of the area below 6 foot 8 inches of each wall, measured from the floor. For the purposes of this code term sunroom as used herein shall include conservatories, sunspaces, solariums, and porch or patio covers or enclosures.

TOWNHOUSE. A single-family dwelling unit constructed in a group of three or more attached units with property lines separating each unit in which each unit extends from foundation to roof and with a yard or public way on at least two sides.

Section R202, Definitions.  Add the following definition. Note that the term is no longer used by the IMC or the IRC:

UNUSUALLY TIGHT CONSTRUCTION. Construction meeting the following requirements:

1.	Walls comprising the building thermal envelope have a continuous water vapor retarder with a rating of 1 perm [57.4 ng/(s · m2 · Pa)] or less with openings therein gasketed or sealed.

2.	Doors and openable windows meet the air leakage requirements of Section N1106; and

3.	Caulking or sealants are applied to areas such as joints around window and door frames between sole plates and floors, between wall-ceiling joints, between wall panels, at penetrations for plumbing, electrical and gas lines, and at other openings.

VALUE. The estimated current replacement cost of the building in kind.

Section R202, Definitions.  Change to read as shown.

WIND-BORNE DEBRIS REGION. Portions of hurricane- prone regions that are within 1 mile (1.61 km) of the coastal mean high water line where the basic wind speed is 110 mph (48 m/s) or greater; or portions of hurricane-prone regions where the basic wind speed is 120 mph (53 m/s) or greater; or Hawaii.

CHAPTER 3  BUILDING PLANNING

R301.1  Change to read as shown:

R301.1 Application. Buildings and structures, and all parts thereof, shall be constructed to safely support all loads, including dead loads, live loads, roof loads, flood loads, snow loads, and wind loads and seismic loads as prescribed by this code. The construction of buildings and structures in accordance with the provisions of this code shall result in a system that provides a complete load path that meets all requirements for the transfer of all loads from their point of origin through the load-resisting elements to the foundation. Buildings and structures constructed as prescribed by this code are deemed to comply with the requirements of this section.

EXCEPTION: Buildings and structures located within the High Velocity Hurricane Zone shall comply only with Sections R302 to R326, inclusive and the provisions of Chapter R44.

R301.2  Change to read as shown:

R301.2 Climatic and geographic design criteria. Buildings shall be constructed in accordance with the provisions of this code as limited by the provisions of this section. Additional criteria shall be established by the local jurisdiction and as set forth in Table R301.2(1).

R301.2.1 Change to read as shown:

R301.2.1 Wind limitations. Buildings and portions thereof shall be limited by wind speed, as defined in Table R301.2(1) and construction methods in accordance with this code. Basic wind speeds shall be determined from Figure R301.2(4). Where different construction methods and structural materials are used for various portions of a building, the applicable requirements of this section for each portion shall apply. Where loads for wall coverings, curtain walls, roof coverings, exterior windows, skylights garage doors and exterior doors (other than garage doors) are not otherwise specified, the loads listed in Table R301.2(2) adjusted for height and exposure using Table R301.2(3) shall be used to determine design load performance requirements for wall coverings, curtain walls, roof coverings, exterior windows, skylights, and exterior doors (other than garage doors). Where loads for garage doors are not otherwise specified, the loads listed in Table R301.2(4) adjusted for height and exposure per Table R301.2(3), shall be used to determine design load performance requirements.  Asphalt shingles shall be designed for wind speeds in accordance with Section R905.2.6.

Overlap with Florida Specific – Structural TAC

Table R301.2(1) Climatic and Geographic Design Criteria.  Change to read as shown. Need to be resolved.

FBC

TABLE R301.2(1)

CLIMATIC AND GEOGRAPHIC DESIGN CRITERIA

| GROUND SNOW LOAD | WIND DESIGN |  | SEISMIC DESIGN CATE- GORYg | SUBJECT TO DAMAGE FROM |  |  |  | WINTER DESIGN TEMPf | ICE SHIELD UNDER- LAYMENT REQUIREDi | FLOOD HAZARDSh | AIR FREEZ-ING INDEXj | MEAN ANNUAL TEMPk |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Speed (mph) | Topo- graphic effectsk |  | Weatheringa | Frost line depthb | Termitec | Decay |  |  |  |  |  |
| NA | See Fig. R301.2(4) |  | NA | Negligible | NA | Very heavy |  |  | NA | See R323 | NA | NA |

For SI: 1 pound per square foot = 0.0479 kN/m2, 1 mile per hour =1.609 km/h.

a. Weathering is “negligible” for concrete as determined from the Weathering Probability Map [Figure 301.2(3)]. The grade of masonry units shall be determined from ASTM C 34, C 55, C 62, C 73, C 90, C 129, C 145, C 216 or C 652.

b. Reserved.

c. Termite infestation per Figure R301.2(6) is “very heavy.”.

d. Wind speed shall be from the basic wind speed map [Figure R301.2(4). Wind exposure category shall be determined on a site-specific basis in accordance with Section R301.2.1.4.

e. The outdoor design dry-bulb temperature shall be selected from the columns of 971/2-percent values for winter from Appendix D of the Florida Building Code, Plumbing. Deviations from the Appendix D temperatures shall be permitted to reflect local climates or local weather experience as determined by the building official.

f. Reserved.

g. Reserved.

h. Reserved.

i. Reserved.

j. Reserved.

k. Reserved.  In accordance with Section R301.2.1.5, where there is local historical data documenting structural damage to buildings due to topographic wind speed-up effects, the jurisdiction shall fill in this part of the table with “YES.” Otherwise, the jurisdiction shall indicate “NO” in this part of the table. (2009 IRC)

Staff recommendation:  should retain Florida Specific provisions.  Recommend keeping Florida Specific provisions by reserving footnote “k” and designating “Topographic effects as “No”.

Figure R301.2(4) Wind Borne Debris Region.  Change to read as shown.

## Figure R301.2(4)

## BASIC WIND DESIGN SPEEDS

Basic Wind Speed

1. Values are nominal design, 3-second gust, wind speeds in mules per hour (mph) at 33 feet (10 m) above ground for Exposure C Category.

2. This map is accurate to the county. Local governments establish specific wind speed/wind-borne debris lines using physical landmarks such as major roads, canals, rivers, and shorelines.

3. Islands and coastal areas outside the last contour shall use the last wind-speed contour of the coastal area.

Table R301.2(4) Garage Door Loads for a Building with a Mean Roof Height of 30 Feet Located in Exposure B.  Add to read as shown.

TABLE R301.2(4)

GARAGE DOOR LOADS FOR A BUILDING WITH A MEAN ROOF HEIGHT OF 30 FEET

LOCATED IN EXPOSURE B

| Basic Wind Speed (mph – 3 second gust) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | 90 | 100 | 110 | 120 | 130 | 140 | 150 |
| Roof Angle > 10 degrees Effective Area: Width (ft) Height (ft) |  |  |  |  |  |  |  |
| - 7 16 7 | 12.8 -14.5 12.3 -13.7 | 15.8 -17.9 15.2 -16.9 | 19.1 -21.6 18.3 -20.4 | 22.8 -25.8 21.8 -24.3 | 26.7 -30.2 25.6 -28.5 | 31.0 -35.1 29.7 -33.1 | 35.6 -40.2 34.1 -38.0 |

For SI: 1 foot = 304.8 mm, 1 square foot = 0.0929 sq m, 1 mile per hour = 1.609 km/h

- For effective areas or wind speeds between those given above the load may be interpolated, otherwise use the load associated with the lower effective area.

- Table values shall be adjusted for height and exposure by multiplying by the adjustment coefficient in Table R301.2(3).

- Plus and minus signs signify pressures acting toward and away from the building surfaces.

- Negative pressures assume door has 2 feet of width in building’s end zone.

R301.2.1.1 Change to read as shown:

R301.2.1.1 Design criteria. Construction in regions where the basic wind speeds from Figure R301.2(4) equal or exceed 100 miles per hour (45 m/s) shall be permitted to be designed in accordance with one of the following:

1.	American Forest and Paper Association (AF&PA) Wood Frame Construction Manual for One- and Two-Family Dwellings (WFCM);

2.	Minimum Design Loads for Buildings and Other Structures (ASCE-7);

3.  	American Iron and Steel Institute (AISI), Standard for Cold-Formed Steel Framing—Prescriptive Method For One- and Two-Family Dwellings (AISI S230).

4.	Concrete and concrete masonry construction shall be designed in accordance with the provisions of this code or in accordance with the applicable documents adopted in Section R301.2.1.1.

5. International Code Council (ICC) Standard for Residential Construction in High Wind Regions (ICC-600);

6.	The FC&PA Guide to Concrete Masonry Residential Construction in High Wind Areas shall be permitted for applicable concrete masonry buildings for a basic wind speed of 130 mph (58 m/s) or less in Exposure B and 110 mph (49 m/s) or less in Exposure C in accordance with Figure R301.2(4);

7.	The WPPC Guide to Wood Construction in High Wind Areas shall be permitted for applicable wood-frame buildings for a basic wind speed of 130 mph (58 m/s) or less in Exposure B and 110 mph (49 m/s) or less in Exposure C in accordance with Figure R301.2(4); or.

8.           The Florida Building Code, Building.

9.  Structural insulated panel (SIP) walls shall be designed in accordance with the provisions of this code.

R301.2.1.1.1 Add to read as follows:

R301.2.1.1.1 Design. The following design guide shall be accepted as conforming to accepted engineering practices: AAF Guide to Aluminum Construction in High-Wind Areas. Vinyl and acrylic panels shall be removable.  Removable panels shall be identified as removable by a decal.  The identification decal shall essentially state: “Removable panel SHALL be removed when wind speeds exceed 75 mph (34 m/s).”  Decals shall be placed such that the decal is visible when the panel is installed.

Section R301.2.1.1.2 Sunrooms, add text to read as follows:

R301.2.1.1.2 Sunrooms. Sunrooms shall comply with AAMA/NPEA/NSA 2100 with the structural requirements and testing provisions of Chapter 5 modified to incorporate ASCE 7. Sunrooms shall be categorized in one of the following categories by the permit applicant, design professional or the property owner where the sunroom is being constructed.

Category I: A roof or a covering of an outdoor space. The openings shall be permitted to be enclosed with insect screening or 0.5 mm (20 mil) maximum thickness plastic film. The space is defined as nonhabitable and unconditioned.

Category II: A roof or a covering of an outdoor space with enclosed walls. The openings are permitted to be enclosed with translucent or transparent plastic or glass. The space is defined as nonhabitable and uunconditioned.

Category III: A roof or a covering of an outdoor space with enclosed walls. The openings are permitted to be enclosed with translucent or transparent plastic or glass. The sunroom complies with additional requirements for forced-entry resistance, air-leakage resistance and water-penetration resistance. The space is defined as nonhabitable and unconditioned.

Category IV: A roof or a covering of an outdoor space with enclosed walls. The sunroom is designed to be heated and/or cooled by a separate temperature control or system and is thermally isolated from the primary structure. The sunroom complies with additional requirements for forced-entry resistance, water penetration resistance, air-leakage resistance, and thermal performance. The space is defined as habitable and conditioned.

Category V: A roof or a covering of an outdoor space with enclosed walls. The sunroom is designed to be heated and/or cooled and is open to the main structure. The sunroom complies with additional requirements for forced-entry resistance, water-penetration resistance, air-leakage resistance, and thermal performance. The space is defined as habitable and conditioned.

Overlap with Florida Specific – Structural TAC

R301.2.1.2 Revise to read as shown:

FBC

R301.2.1.2 Protection of openings.  Windows in buildings located in wind-borne debris regions shall have glazed openings protected from wind-borne debris.  Glazed opening protection for wind-borne debris shall meet the requirements of the Large Missile Test of an approved impact resisting standard or ASTM E 1996 and ASTM E 1886, SSTD 12, ANSI/DASMA 115 (for garage doors) or TAS 201, 202 and 203 or AAMA 506 referenced therein.

(1)	Opening in sunrooms, balconies or enclosed porches constructed under existing roofs or decks are not required to be protected provided the spaces are separated from the building interior by a wall and all openings in the separating wall are protected in accordance with this section. Such space shall be permitted to be designed as either partially enclosed or enclosed structures.

(2)	Storage sheds that are not designed for human habitation and that have a floor area of 720 square feet (67 m2) or less are not required to comply with the mandatory wind-borne debris impact standard of this code.

Impact resistant coverings shall be tested at 1.5 times the design pressure (positive or negative) expressed in pounds per square feet as determined by the Florida Building Code, Residential Section R301 for which the specimen is to be tested.

Exception: Wood structural panels with a minimum thickness of 7/16 inch (11.1 mm) and a maximum span of 8 feet (2438 mm) shall be permitted for opening protection in one- and two-story buildings. Panels shall be precut so that they shall be attached to the framing surrounding the opening containing the product with the glazed openings. Panels shall be predrilled as required for the anchorage method and all required hardware shall be provided. Permanent corrosion resistant attachment hard ware with anchors permanently installed on the building shall be provided and designed to resist the component and cladding loads determined in accordance with the provisions of the Florida Building Code, Building. Attachment in accordance with Table R301.2.1.2 with permanent corrosion resistant attachment hardware provided and anchors permanently installed on the building is permitted for buildings with a mean roof height of 45 feet (10 058 mm) or less where wind speeds do not exceed 140 miles per hour (58 m/s).

IRC ’09 is changed as follows. Resolve potential conflicts. Need to be resolved.

R301.2.1.2 Protection of openings. Windows in buildings located in windborne debris regions shall have glazed openings protected from windborne debris. Glazed opening protection for windborne debris shall meet the requirements of the Large Missile Test of  an approved impact resisting standard or ASTM E 1996 and ASTM E 1886 referenced therein. Garage door glazed opening protection for windborne debris shall meet the requirements of an approved impact resisting standard or ANSI/DASMA 115.

Exception: Wood structural panels with a minimum thickness of 7/16 inch (11 mm) and a maximum span of 8 feet (2438 mm) shall be permitted for opening protection in one- and two-story buildings. Panels shall be precut so that they shall be and attached to the framing surrounding the opening containing the product with the glazed opening. Panels shall be predrilled as required for the anchorage method and shall be secured with the attachment hardware provided. Attachments shall be designed to resist the component and cladding loads determined in accordance with either Table R301.2(2) or ASCE 7, with the permanent corrosion resistant attachment hardware provided and anchors permanently installed on the building. Attachment in accordance with Table R301.2.1.2 is permitted for buildings with a mean roof height of 33 feet (10 058 mm) or less where wind speeds do not exceed 130 miles per hour (58 m/s).

Staff recommendation:  With regard to R301.2.1.2, recommend using the IRC09 language as the base provisions and then revising the text to add the reference to SSTD 12, TAS 202, 202, 203 and AAMA 506.  With regard to the “Exception”, the IRC09 covers the Florida specific requirements and for that recommend using the IRC09 requirements instead.

Overlap with Florida Specific – Structural TAC

FBC

Table R301.2.1.2 Change to read as shown:

# TABLE R301.2.1.2

WIND-BORNE DEBRIS PROTECTION FASTENING SCHEDULE

FOR WOOD STRUCTURAL PANELS

| ## FASTENER TYPE | FASTENER SPACING (in.)1,2 |  |  |  |
| --- | --- | --- | --- | --- |
|  | Panel span ≤ 2 ft | 2 foot < panel span ≤ 4 foot | 4 foot < panel span ≤ 6 foot | 6 foot < panel span ≤ 8 foot |
| #8 Wood Screw based anchor with 2-inch embedment length3 | 16 | 16 | 10 | 8 |
| #10 Wood Screw based anchor with 2-inch embedment length | 16 | 16 | 12 | 9 |
| ¼ Lag screw based anchor with 2-inch embedment length3 | 16 | 16 | 16 | 16 |

SI: 1 inch = 25.4 mm, 1 foot = 305 mm.

1. This table is based on a maximum wind speed of 140  mph (58 m/s) and mean roof height of 45 feet (10 m) or less.

2. Fasteners shall be installed at opposing ends of the wood structural panel. [IRC ’06 footnote “c” not used]

3. Where screws are attached to masonry or masonry/stucco, they shall  be attached using vibration-resistant anchors having a minimum withdrawal capacity of 1500 lb (2180 kN).

IRC ’09 Table R301.2.1.2 is changed to more closely follow the Florida table. Some previously FL-specific criteria are no longer high-lighted.  Resolve potential conflicts.

a. This table is based on 130 mph wind speeds and a 33-footmean roof height.

b. Fasteners shall be installed at opposing ends of the wood structural panel. Fasteners shall be located a minimum of 1 inch from the edge of the panel.

c. Anchors shall penetrate through the exterior wall covering with an embedment length of 2 inches minimum into the building frame. Fasteners

shall be located a minimum of 21/2 inches from the edge of concrete block or concrete.

d. Where panels are attached to masonry or masonry/stucco, they shall be attached using vibration-resistant anchors having a minimum ultimate withdrawal capacity of 1500 pounds.

Staff recommendation:  The IRC09 covers the Florida specific requirements and for that recommend using the IRC09 requirements instead.

Overlap with Florida Specific – Structural TAC

Section R301.2.1.4 Exposure category, revise text to read as follows:

FBC

R301.2.1.4 Exposure category. For each wind direction considered, an exposure category that adequately reflects the characteristics of ground surface irregularities shall be determined for the site at which the building or structure is to be constructed. For a site located in the transition zone between categories, the category resulting in the largest wind forces shall apply. Account shall be taken of variations in ground surface roughness that arise from natural topography and vegetation as well as from constructed features. For any given wind direction, the exposure in which a specific building or other structure is sited shall be assessed as being one of the following categories:

Exception: An intermediate exposure between the exposure categories defined is permitted in a transition zone provided that it is determined by a rational analysis method.

- Exposure A. This exposure category is not applicable in Florida.

2.	Exposure B. Urban and suburban areas, wooded areas or other terrain with numerous closely spaced obstructions having the size of single-family dwellings or larger. Exposure B shall be assumed unless the site meets the definition of another type of exposure.

- Exposure C. Open terrain with scattered obstructions, including surface undulations or other irregularities, having heights generally less than 30 feet (9144 mm) extending more than 1,500 feet (457.2 m) from the building site in any quadrant. This exposure shall also apply to any building located within Exposure B-type terrain where the building is within 100 feet horizontally in any direction of open areas of Exposure C-type terrain that extends more than 600 feet (182.9 m) and width greater than 150 ft in the upwind direction. Short term (less than two year) changes in the pre-existing terrain exposure, for the purposes of development, shall not be considered open fields. Where development build out will occur within 3 years and the resultant condition will meet the definition of Exposure B, Exposure B shall be regulating for the purpose of permitting.  This category includes flat open country, grasslands, and ocean or gulf shorelines and shall extend downwind for a distance of 1500 feet. For buildings located within a distance of 600 feet of inland bodies of water that present a fetch of 1 mile (1.61 km) or more or inland waterways or rivers with a width of 1 mile (1.61 km) or more roof sheathing uplift and roof-to-wall uplift loads shall be increased by 20%.

- Exposure D. This exposure category is not applicable in Florida.

IRC ’09 has been changed as shown. Resolve potential conflicts.

R301.2.1.4 Exposure category. For each wind direction considered, an exposure category that adequately reflects the characteristics of ground surface irregularities shall be determined for the site at which the building or structure is to be constructed. For a site located in the transition zone between categories, the category resulting in the largest wind forces shall apply. Account shall be taken of variations in ground surface roughness that arise from natural topography and vegetation as well as from constructed features. For a site where multiple detached one- and two-family dwellings, townhouses or other structures are to be constructed as part of a subdivision, master-planned community, or otherwise designated as a developed area by the authority having

jurisdiction, the exposure category for an individual structure shall be based upon the site  conditions that will exist at the time when all adjacent structures on the site have been constructed, provided their construction is expected to begin within one year of the start of construction  for the structure for which the exposure category is determined. For any given wind direction, the exposure in which a specific building or other structure is sited shall be assessed as being one of the following categories:

[No change to 1 – 4.]

Staff recommendation:  With regard to R301.2.1.4, recommend using the IRC09 language as the base and then add to it Florida specific “Exception “ stated above.  The Exception is not covered by the IRC09.   However, with regard to the “Exposures” use Florida specific provisions of Items 1 through 4 as stated above.  The IRC09 does no cover Florida specific provisions with regard to exposures.

Section R301.2.1.4.1 Wind directions and sectors, add text to read as follows:

R301.2.1.4.1 Wind directions and sectors. For each selected wind direction at which the wind loads are to be evaluated, the exposure of the building or structure shall be determined for the two upwind sectors extending 45 degrees (0.79 rad) either side of the selected wind direction. The exposures in these two sectors shall be determined in accordance with Sections R301.2.4.2 and R301.2.1.4.3 and the exposure resulting in the highest wind loads shall be used to represent winds from that direction.

Section R301.2.1.4.2 Surface roughness categories, add text to read as follows:

R301.2.1.4.2 Surface roughness categories. A ground surface roughness within each 45-degree 4(0.79 rad) sector shall be determined for a distance upwind of the site as defined in Section R301.2.1.4.3 from the categories defined below, for the purpose of assigning an exposure category as defined in Section R301.2.1.4.3.

Surface Roughness B. Urban and suburban areas, wooded areas or other terrain with numerous closely spaced obstructions having the size of single-family dwellings or larger.

Surface Roughness C. Open terrain with scattered obstructions having heights generally less than 30 feet (9144 mm). This category includes flat open country, grasslands, and all water surfaces in hurricane-prone regions.  This surface roughness shall also apply to any building located within surface roughness B-type terrain where the building is within 100 feet horizontally in any direction of open areas of surface roughness C-type terrain that extends more than 600 feet (182.9 m) and width greater than 150 ft. in the upwind direction. Short-term (less than two year) changes in the pre-existing terrain exposure, for the purposes of development, shall not be considered surface roughness C. Where development buildout will occur within three years and the resultant condition will meet the definition of surface roughness B, surface roughness B shall be regulating for the purpose of permitting. This category includes flat open country, grasslands and ocean or gulf shorelines and shall extend downwind for a distance of 1500 feet.

Surface Roughness D. Reserved.

Section R301.2.1.4.3 Exposure categories, add text to read as follows:

R301.2.1.4.3 Exposure categories. An exposure category shall be determined in accordance with the following:

1. Exposure B. Exposure B shall apply where the ground surface roughness condition, as defined by Surface Roughness B, prevails in the upwind direction for a distance of at least 2,600 feet (792 m) or 20 times the height of the building, whichever is greater.

Exception: For buildings whose mean roof height is less than or equal to 30 feet (9144 mm), the upwind distance is permitted to be reduced to 1,500 feet (457 m).

2.  Exposure C.  Exposure C shall apply for all cases where Exposure B does not apply. Buildings located within a distance of 600 feet of inland bodies of water that present a fetch of 1 mile (1.61 km) or more or inland waterways or rivers with a width of 1 mile (1.61 km) or more shall be classified as Exposure C and roof sheathing uplift and roof-to-wall uplift loads shall be increased by 20 percent.

3.  Exposure D.  This exposure category is not applicable in Florida.

R301.2.1.6 Add to read as shown:

R301.2.1.6 Basic wind speed. The basic wind speed in miles per hour, for the development of windloads, shall be determined from Figure R301.2(4). The exact location of wind speed lines shall be established by local ordinance using recognized physical landmarks such as major roads, canals, rivers and lake shores whenever possible.

Change the following sections to read as follows:

R301.2.2 Seismic provisions. Reserved.

Figure R301.2(2)  Reserved.

R301.2.3 Snow loads. Reserved.

Figure R301.2(5) Reserved.

R301.2.5 Add to read as follows:

R301.2.5 Structures seaward of a coastal construction line. Structures located seaward of the coastal construction line shall be designed to resist the predicted forces of a 100-year storm event in accordance with Section 3109 of the Florida Building Code, Building.

Section R301.3 Story height.  Change to read as shown.

R301.3 Story height. Buildings constructed in accordance with these provisions shall be limited to story heights of not more than the following:

1. For conventional light-frame wood construction, the laterally unsupported bearing wall stud height permitted by Table R602.2(5) plus a height of floor framing not to exceed sixteen inches. For purposes of determining uplift, gravity loads, and lateral bracing requirements, an attic shall be considered an additional story when the roof slope is 6 in 12 or greater. (See Figure R301.3).

Exception: For wood framed wall buildings with bracing in accordance with Table R602.2.10.1, the wall stud clear height used to determine the maximum permitted story height may be increased to 12 feet (3658 mm) without requiring an engineered design for the building wind and seismic force resisting systems provided that the length of bracing required by Table R602.2.10.1 is increased by multiplying by a factor of 1.20. Wall studs are still subject to the requirements of this section.

[IRC ’09 R301.3 Exception is revised to add another seismic criteria table. No apparent impact.]

2-5 No change.

Individual walls or walls studs shall be permitted to exceed these limits as permitted by Chapter 6 provisions for buildings where the wind speed is less than 100 mph (160.9 km/h), provided story heights are not exceeded. Floor framing height shall be permitted to exceed these limits provided the story height does not exceed 11 feet 7 inches (3531 mm).  An engineered design shall be provided for the wall or wall framing members when they exceed the limits of Chapter 6. Where the story height limits are exceeded, an engineered design shall be provided in accordance with the Florida Building Code, Building for the overall wind force resisting systems.

Figure R301.3, add the figure and credit as shown below [delete DRAFT/copyright overlay???]:

Courtesy, American Forest and Paper Association, Washington, D.C.

R301.6 Change to read as shown:

R301.6 Roof load. The roof shall be designed for the live load indicated in Table R301.6 or the snow load…greater..

SECTION R302

FIRE RESISTANT CONSTRUCTION

IRC ’09 Section 302 has been extensively changed. Section 302.1 is shown below, with Florida specific criteria. Resolve potential conflicts.

R302.1 Exterior walls. Construction, projections, openings and penetrations of exterior walls of dwellings and accessory buildings shall comply with Table R302.1.

Exceptions:

1. Walls, projections, openings or penetrations in walls perpendicular to the line used to determine the fire separation distance.

2. Walls of dwellings and accessory structures located on the same lot.

3. Detached tool sheds and storage sheds, playhouses and similar structures exempted from permits are not required to provide wall protection based on location on the lot. Projections beyond the exterior wall shall not extend over the lot line.

4. Detached garages accessory to a dwelling located within 2 feet (610 mm) of a lot line are permitted to have roof eave projections not exceeding 4 inches (102 mm).

5. Foundation vents installed in compliance with this code are permitted.

6. Openings and roof overhang projections shall be permitted on the exterior wall of a building located on a zero lot line when the building exterior wall is separated from an adjacent building exterior wall by a distance of 6 feet or more, and the roof overhang projection is separated from an adjacent building projection by a distance of 4 feet or more, with 1 hour fire resistive construction on the underside of the overhang required, unless the separation between projections is 6 feet or more.

Overlap with Florida Specific – Fire TAC

Table R302.1 IRC, Exterior Walls, has been revised (in red). Consider potential conflicts.

Table R302.1

EXTERIOR WALLS

| EXTERIOR WALL ELEMENT |  | MINIMUM FIRE-RESISTANCE RATING | MINIMUM FIRE SEPARATION DISTANCE |
| --- | --- | --- | --- |
| Walls | (Fire-Resistance Rated) | 1 hour-tested in accordance with ASTM E 119 or UL 263 with exposure form both sides | 5 0 feet |
|  | ( Not Fire-Resistance Rated) | 0 Hours | ≤5 3 feet |
| Projections | (Fire-Resistance Rated) | 1 hour on the underside | ≥2 to 5 2 feet |
|  | Not (Fire-Resistance Rated) | 0 Hours | 3 feet |
| Openings | Not Allowed | N/A | <3 feet N/A |
|  | 25% Maximum Wall Area | 0 Hours | 3 feet |
|  | Unlimited | 0 Hours | 5 3 feet |
| Penetrations | All | Comply with Section R317.3 | <5 <3 feet |
|  |  | None Required | 5 3 feet |

N/A = Not Applicable.

Staff recommendation:  Florida specific provisions are not covered by the IRC09.  Recommend retaining Florida specific provisions as stated above.

R302.2.2 [was R317.2.2] Parapets. Change to read as follows:

R302.2.2 Parapets.  Parapets constructed in accordance with Section R302.2.3 shall be provided for townhouses as an extension of exterior walls or common walls in accordance with the following:

1.	Where roof surfaces adjacent to the wall or walls are at the same elevation, the parapet shall extend not less than 18 inches (457.2 mm) above the roof surfaces.

2.	Where roof surfaces adjacent to the wall or walls are at different elevations and the higher roof is not more than 18 inches (457.2 mm) above the lower roof, the parapet shall extend not less than 18 inches (762 mm) above the lower roof surface.

Exception: A parapet is not required in the two cases above when the roof is covered with a minimum class C roof covering, and the roof decking or sheathing is of noncombustible materials or approved fire-retardant-treated wood for a distance of 4 feet (1219 mm) on each side of the wall or walls, or one layer of 5/8-inch (15.9 mm) Type X gypsum board is installed directly beneath the roof decking or sheathing, supported by a minimum of nominal 2-inch (51 mm) ledgers attached to the sides of the roof framing members, for a minimum distance of 4 feet (1220 mm) on each side of the wall or walls.

3. A parapet is not required where roof surfaces adjacent to the wall or walls are at different elevations and the higher roof is more than 18 inches (457.2 mm) above the lower roof. The common wall construction from the lower roof to the underside of the higher roof deck shall not have less than a 1-hour fire-resistive rating. The wall shall be rated for exposure from both sides.

R302.2.3 [was 317.2.3] Change to read as follows:

R302.2.3 Parapet construction. Parapets shall have the same fire-resistance rating as that required for the supporting wall or walls. On any side adjacent to a roof surface, the parapet shall have noncombustible faces for the uppermost 18 inches (457 mm), to include counterflashing and coping materials. Where the roof slopes toward a parapet at slopes greater than two units vertical in 12 units horizontal (16.7-percent slope), the parapet shall extend to the same height as any portion of the roof within a distance of 3 feet (914 mm), but in no case shall the height be less than 18 inches (457 762 mm).

R302.4.2 [was 317.3.2] Change to read as follows:

Section R302.4.2 Membrane penetrations. Membrane penetrations shall comply with Section R302.4.1. Where walls are required to have a minimum fire-resistance rating, recessed fixtures shall be so installed such that the required fire resistance will not be reduced.

Exceptions: No change.

R302.5.2 [was R309.1.1] Duct penetration. Change to read as follows:

R302.5.2 Duct penetration. Ducts in the garage and ducts penetrating the walls or ceilings separating the dwelling from the garage shall be constructed of a minimum No. 26 gage (0.48 mm) sheet steel, 1 inch minimum rigid nonmetallic Class 0 or Class 1 duct board, or other approved material and shall have no openings into the garage.

R302.10.4 [was 316.4] Expanded attic insulation. Change to read as follows:

R302.10.4 Exposed attic insulation. All exposed insulation materials installed on attic floors shall have a critical radiant flux not less than 0.12 watt per square centimeter. Exposed foam plastic insulation materials exposed on the underside of the roof deck or on the attic walls shall comply with R316.

Section R306.3 Sewage disposal, revise text to read as follows:

R306.3 Sewage disposal. All plumbing fixtures shall be connected to a sanitary sewer or to an approved private sewage disposal system in accordance with Chapter 64E-6, Florida Administrative Code, Standards for Onsite Sewage Treatment and Disposal Systems.

Section R308.1 Identification, revise text to read as follows:

R308.1 Identification. Each pane shall bear the manufacturer’s label designating the type and thickness of glass or glazing material. Except as indicated in Section R308.1.1, each pane of glazing installed in hazardous locations as defined in Section R308.4 shall be provided with a manufacturer’s or installer’s label, designating the type and thickness of glass and the safety glazing standard with which it complies, which is visible in the final installation. The safety glazing label shall be acid etched, sandblasted, ceramic-fired, embossed mark, or shall be of a type which once applied cannot be removed without being destroyed. Laminated glass, other than as used for safety glazing, shall be permanently identified as per this section, designating laminator, overall glass thickness and trade name of interlayer.

Exceptions:

1. For other than tempered glass, labels may be omitted provided the building official approves the use of a certificate, affidavit or other evidence furnished by the glazing contractor certifying that each light is glazed in accordance with approved construction documents that comply with the provisions of this chapter confirming compliance with this code.

2. Tempered spandrel glass may be identified by the manufacturer with a removable paper label.

Section R308.6.9 [was R613.3.1.1] Testing and labeling.  Change to read as shown.

R308.6.9 Testing and labeling of skylights. Exterior skylights shall be tested by an approved independent testing laboratory, and shall be labeled to indicate compliance with the requirements of one of the following specification:

ANSI/AAMA/WDMA 101/I.S.2/NAFS or AAMA/WDMA/CSA 101/I.S.2/A440, or TAS 202 (HVHZ shall comply with TAS 202).

Exterior skylights shall be labeled with a permanent label, marking, or etching providing traceability to the manufacturer and product. The following shall also be required either on a permanent label or on a temporary supplemental label applied by the manufacturer: information identifying the manufacturer, the product model/series number, positive and negative design pressure rating, product maximum size, type and thickness of glass or glazing material, impact-resistance rating if applicable, Florida Product Approval number or Miami-Dade Product Approval number, applicable test standard(s), and approved product certification agency, testing laboratory, evaluation entity or Miami-Dade Product Approval.

Labels are limited to one design pressure rating per reference standard. The temporary supplemental label shall remain on the skylight until final approval by the building official.

R310.1 Change to read as follows:

R310.1 Emergency escape and rescue required.  Change exceptions to as follows.

Exceptions:

1. Basements used only to house mechanical equipment and not exceeding total floor area of 200 square feet (18.58 m2).

2. The emergency escape and rescue opening shall be permitted to open into a screen enclosure, open to the atmosphere, where a screen door is provided leading away from the residence.

R310.4 Change to read as follows:

R310.4 Bars, grills, covers and screens.  Bars, grills, covers, screens or similar devices are permitted to be placed over emergency escape and rescue openings, bulkhead enclosures, or window wells that serve such openings, provided the minimum net clear opening size complies with Sections R310.1.1 to R310.1.3, and such devices shall be releasable or removable from the inside without the use of a key, tool, special knowledge or force greater than that which is required for normal operation of the escape and rescue opening. The temporary installation or closure of storm shutters, panels, and other approved hurricane protection devices shall be permitted on emergency escape and rescue openings during the threat of a storm. Such devices shall not be required to comply with the operational constraints of Section R310.1.4. While such protection is provided, at least one means of escape from the dwelling or dwelling unit shall be provided. The means of escape shall be within the first floor of the dwelling or dwelling unit and shall not be located within a garage without a side-hinged door leading directly to the exterior. Occupants in any part of the dwelling or dwelling unit shall be able to access the means of escape without passing through a lockable door not under their control.

Overlap with Florida Specific – Fire TAC

FBC

Section R311.4.3 Landings at doors.  Change to read as shown.

R311.4.3 Landings at doors.  There shall be a floor or landing on each side of each exterior door. The floor…2-percent.

Exceptions:

1. Where a stairway of two or fewer risers is located on the exterior side of a door other than the required exit door, a landing is not required for the exterior side of the door other than…stairway.

2 – 3. [Deleted]

The floor or landing at exterior doors required by Section R311.4.1 shall not be required to comply with this requirement but shall have a rise no greater than that permitted in Section R311.5.3.

The width of each landing shall not be less than the door served. Every landing shall have a minimum dimension of 36 inches (914 mm) measured in the direction of travel.

2009 IRC 311.4.3 is moved to R311.3 to read as shown. Resolve potential conflicts.

R311.3 Floors and landings at exterior doors. There shall be a landing or floor on each side of each exterior door. The width of each landing shall not be less than the door served. Every landing shall have a minimum dimension of 36 inches (914 mm) measured in the direction of travel. Exterior landings shall be permitted to have a slope not to exceed 1/4 unit vertical in 12 units horizontal (2-percent).

Exception: Exterior balconies less than 60 square feet (5.6 m2) and only accessible from a door are permitted to have a landing less than 36 inches (914 mm) measured in the direction of travel.

R311.3.1 Floor elevations at the required egress doors. Landings or floors at the required egress door shall not be more than 1-1/2 inches (38 mm) lower than the top of the threshold.

Exception: The exterior landing or floor shall not be more than 7-3/4 inches (196 mm) below the top of the threshold provided the door does not swing over the landing or floor.

When exterior landings or floors serving the required egress door are not at grade, they shall be provided with access to grade by means of a ramp in accordance with Section R311.8 or a stairway in accordance with Section R311.7.

R311.3.2 Floor elevations for other exterior doors. Doors other than the required egress door shall be provided with landings or floors not more than 7-3/4 inches (196 mm) below the top of the threshold.

Exception: A landing is not required where a stairway of two or fewer risers is located on the exterior side of the door, provided the door does not swing over the stairway.

R311.3.3 Storm and screen doors. Storm and screen doors shall be permitted to swing over all exterior stairs and landings.

Staff recommendation:  Florida specific requirements are not covered by the IRC09.  Recommend retaining Florida specific provisions stated above.

R311.5.3.2 Tread depth. The minimum tread depth, exclusive of nosing, shall be not less than 9 inches (229 mm). Treads and risers of stairs shall be permitted to be so proportioned that the sum of two risers and a tread, exclusive of projection of nosing, is not less than 24 inches (610 mm) nor more than 25 inches (635 mm). The tread depth shall be measured horizontally between the vertical planes of the foremost projection of adjacent treads and at a right angle to the tread’s leading edge. The greatest tread depth within any flight of stairs shall not exceed the smallest by more than 3/8 inch (9.5 mm). Winder treads shall have a minimum tread depth of 10 inches (254 mm) measured as above at a point 12 inches (305) mm from the side where the treads are narrower. Winder treads shall have a minimum tread depth of 6 inches (152 mm) at any point. Within any flight of stairs, the greatest winder tread depth at the 12 inch (305 mm) walk line shall not exceed the smallest by more than 3/8 inch (9.5 mm).

IRC ’09 moved Section R311.5.3.2 to R311.7.4.2 and changed it to read as shown. Resolve potential conflicts.

R311.7.4.2 Tread depth. The minimum tread depth shall, exclusive of nosing, shall be not less than 9 inches (229 mm). Treads and risers of stairs shall be permitted to be so proportioned that the sum of two risers and a tread, exclusive of projection of nosing, is not less than 24 inches (610 mm) nor more than 25 inches (635 mm).  The tread depth shall be measured horizontally between the vertical planes of the foremost projection of adjacent treads and at a right angle to the tread's leading edge. The greatest tread depth within any flight of stairs shall not exceed the smallest by more than 3/8 inch (9.5 mm). Consistently shaped winders at the walkline shall be allowed within the same flight of stairs as rectangular treads and do not have to be within 3/8 inch (9.5 mm) of the rectangular tread depth.

Winder treads shall have a minimum tread depth of 10 inches (254 mm) measured between the vertical planes of the foremost projection of adjacent treads at the intersections with the walkline. Winder treads shall have a minimum tread depth of 6 inches (152 mm) at any point within the clear width of the stair. Within any flight of stairs, the largest winder tread depth at the  walkline shall not exceed the smallest winder tread by more than 3/8 inch (9.5 mm).

R311.7.4.3 [was 311.5.3.2] Change to read as follows:

R311.7.4.3 5.3.3 Profile. The radius of curvature at the leading edge of the tread shall be no greater than 9/16 inch (14.3 mm). Every tread less than 10 inches (254 mm) wide shall have a nosing or effective projection of approximately 1 inch (25 mm) over the level immediately below that tread. Beveling of nosing shall not exceed ½ inch (12.7 mm). Risers shall be vertical or sloped from the underside of the leading edge of the tread above at an angle not more than 30 (0.51 rad) degrees from the vertical. Open risers are permitted, provided that the opening between treads does not permit the passage of a 4-inch diameter (102 mm) sphere.

Exceptions:

1.	A nosing is not required where the tread depth is a minimum of 11 inches (279 mm).

2.	The opening between adjacent treads is not limited on stairs with a total rise of 30 inches (762 mm) or less.

R311.7.5 [was 311.5.4] Landings for stairways. Change to read as follows:

R311.7.5 .5.4 Landings for stairways. There shall be a floor or landing at the top and bottom of each stairway.

Exception: A door at the top of a stair shall be permitted to open directly at a stair, provided the door does not swing over the stair.

A flight of stairs shall not have a vertical rise greater than 12 feet (3658 mm) between floor levels or landings.

The width of each landing shall not be less than the stairway served. Every landing shall have a minimum dimension of 36 inches (914 mm) measured in the direction of travel.

Overlap with Florida Specific – Fire TAC

R311.7.7 [was 311.5.6] Handrails. Change to read as follows: need to be resolved.

R311.7.7.1 Height. Handrail height, measured vertically from the sloped plane adjoining the tread nosing, or finish surface of ramp slope, shall be not less than 34 inches (864 mm) and not more than 38 inches (965 mm).

Exception: When fittings are used to provide transition between flights, transition from handrail to guardrail, or used at the start of a stair, the handrail height at the fitting. shall be permitted to exceed the maximum height.

Exceptions:

1. The use of a volute, turnout or starting easing shall be allowed over the lowest tread.

2. When handrail fittings or bendings are used to provide continuous transition between flights, the transition from handrail to guardrail, or used at the start of a flight, the handrail height at the fittings or bendings shall be permitted to exceed the maximum height.

Staff recommendation:  The IRC09 covers Florida specific requirements.  Recommend using the IRC09 provisions instead of the Florida specific provisions as stated above.

R311.7.7.2 Continuity. Handrails for stairways shall be continuous for the full length of the flight, from a point directly above the top nosing edge of the flight to a point directly above the lowest nosing edge of the flight. Handrail ends shall be returned or shall terminate in newel posts or safety terminals. Handrails adjacent to a wall shall have a space of no less than 1-1/2 inch (38 mm) between the wall and the handrails.

Exceptions:

- Handrails shall be permitted to be interrupted by a newel post at the turn and at the top of the flight.

- The use of a volute, turnout, starting easing or newel shall be allowed over the lowest tread.

R311.7.9.1 [was 311.5.8.1] Spiral stairways. Change to read as follows.

R311.7.9.1 Spiral stairways. Spiral stairways are permitted, provided the minimum width shall be 26 inches (660 mm) with each tread having a 7½-inches (190 mm) minimum tread depth at 12 inches from the narrower edge. All treads shall be identical, and the rise shall be no more than 9½ inches (241 mm). A minimum headroom of 6 feet 6 inches (1982 mm) shall be provided. Handrails shall be provided on one side.

R311.7.9.3 [was 311.5.8.3] Add to read as follows:

R311.7.9.3 Circular stairways. Circular stairs may have a minimum tread depth of 9 inches (229 mm) with 1 inch (25.4 mm) of nosing, and the smaller radius may be less than twice the width of the stairway.

SECTION R313

AUTOMATIC FIRE SPRINKLER SYSTEMS

Add Section [was 324] to read as shown.

SECTION R31324

FIRE PROTECTION

Overlap with Florida Specific – Fire TAC

FBC

R324.1 Sprinkler system requirements for buildings three stories or more in height.  NFPA 101 as adopted by the Florida Fire Prevention Code, as regarding the requirements for fire protection sprinklers, is applicable to all multiple-family residential buildings, whether designated as townhouses, condominiums, apartment houses, tenements, garden apartments or by any other name. The attorney general has determined that for the purpose of the fire protection sprinkler requirements in Section 553.895(2), Florida Statutes, townhouses that are three or more stories tall and consist of three or more units together are multiple-family dwellings. Therefore, these types of townhouses are not exempt from being considered for the requirements to provide fire protection sprinklers (even if there are any other definitions that define townhouse as single-family residences). When determining whether townhouses require fire protection sprinkler systems, the building official must consider in parallel: (a) the attorney general’s opinion defining the statutory language for townhouses; (b) the building code requirements, including all life-safety chapters, that provide additional determining criteria, such as construction types, fire-resistance, fire protection systems and egress; and (c) the NFPA 101 as adopted by the Florida Fire Prevention Code egress and protection determining criteria. The more restrictive criteria are then applied.

IRC ’09, has been added/changed as shown. Resolve potential conflicts.

R313.1 Townhouse automatic fire sprinkler systems. An automatic residential fire sprinkler system shall be installed in townhouses.

Exception: An automatic residential fire sprinkler system shall not be required when additions or alterations are made to existing townhouses that do not have an automatic residential fire sprinkler system installed.

R313.1.1 Design and installation. Automatic residential fire sprinkler systems for townhouses shall be designed and installed in accordance with Section P2904.

R313.2 One- and two-family dwellings automatic fire systems. Effective January 1, 2011, an automatic residential fire sprinkler system shall be installed in one- and two- family dwellings.

Exception: An automatic residential fire sprinkler system shall not be required for additions or alterations to existing buildings that are not already provided with an automatic residential sprinkler system.

R313.2.1 Design and installation. Automatic residential fire sprinkler systems shall be designed and installed in accordance with Section P2904 or NFPA 13D.

Staff recommendation:  The IRC09 covers Florida specific provisions for sprinkler system as stated above.  Recommend using the IRC09 provisions instead of Florida specific provisions.

SECTION R314

SMOKE ALARMS

Overlap with Florida Specific – Mechanical TAC / Fire TAC

[This section is rewritten; the only Florida-specific text should be moved to 315, Carbon Monoxide Alarms]

FBC

Section R315 [was 313] SMOKE ALARMS.

Section R315.1 Add text to read as follows:

R315.1 4 Carbon monoxide protection.  Every building for which a permit for new construction is issued having a fossil-fuel-burning heater or appliance, a fireplace, or an attached garage shall have an operational carbon monoxide alarm installed within 10 feet of each room used for sleeping purposes.

R315.1.1 Power Source. In new construction, alarms shall receive their primary power from the building wiring when such wiring is served from the local power utility. Such alarms shall have battery back up.

R315.1.2 Combination alarms. Combination smoke/carbon monoxide alarms shall be listed or labeled by a Nationally Recognized Testing Laboratory.

IRC ’09 is changed to add the following. Resolve potential conflicts.

SECTION R315

CARBON MONOXIDE ALARMS

R315.1 Carbon monoxide alarms. For new construction, an approved carbon monoxide alarm shall be installed outside of each separate sleeping area in the immediate vicinity of the bedrooms in dwelling units within which fuel-fired appliances are installed and in dwelling units that have attached garages.

R315.2 Where required in existing dwellings. Where work requiring a permit occurs in existing dwellings that have attached garages or in existing dwellings within which

fuel-fired appliances exist, carbon monoxide alarms shall be provided in accordance with Section R315.1.

R315.3 Alarm requirements. Single station carbon monoxide alarms shall be listed as complying with UL 2034 and shall be installed in accordance with this code and the manufacturer’s installation instructions

Staff recommendation:  Florida specific provisions for Carbon monoxide are not fully covered by the IRC09.  Recommend retaining Florida specific requirements as stated above.

R316 [was 314] FOAM PLASTIC.

R316.1 [was 314.1] General. Change to read as follows:

R316.1 General. The provisions of this section shall govern materials, design, application, construction and installation of foam plastic materials.

Overlap with Florida Specific – Structural  TAC

FBC

R316.3 [was 314.3] Surface burning characteristics. Change to read as follows:

R316.3 Surface burning characteristics. Unless otherwise allowed in Section R316.5 or Section R316.6, all foam plastic or foam plastic cores in manufactured assemblies used as a component in manufactured assemblies used in building construction shall have a flame-spread index of not more than 75 and shall have a smoke-developed index of not more than 450 when tested in the maximum thickness of 4 inches (102 mm), provided the end use is approved in accordance with Section R316.6 using the thickness and density intended for use intended for use in accordance with ASTM E 84. Loose-fill type foam plastic insulation shall be tested as board stock for the flame spread index and smoke-developed index.

Exception:  Foam plastic insulation greater than 4 inches in thickness shall have a maximum flame spread index of 75 and a smoke-developed index of 450 where tested at a minimum thickness of 4 inches, provided the end use is approved in accordance with Section R3164.8 using the thickness and density intended for use.

IRC ’09 is changed to read as follows. Resolve potential conflicts.

R316.3 Surface burning characteristics. Unless otherwise allowed in Section R316.5 or R316.6, all foam plastic or foam plastic cores used as a component in manufactured assemblies used in building construction shall have a flame spread index of not more than 75 and shall have a smoke-developed index of  not more than 450 when tested in the maximum thickness intended for use in accordance with ASTM E 84 or UL 723. Loose-fill type foam plastic insulation shall be tested as board stock for the flame spread index and smoke-developed index.

[No change to exception]

Staff recommendation: The IRC09 covers Florida specific provisions for loose-type foam plastic.  Recommend using the IRC09 provisions instead of Florida specific provisions as stated above.

R316.5 [was 314.5] Specific requirements.

R316.5.1 [was 314.5.1] Masonry or concrete construction. Change to read as follows:

R316.5.1 Masonry or concrete construction. The thermal barrier specified in Section R316.4 is not required in a masonry or concrete wall, floor or roof when the foam plastic insulation is protected on each face by a minimum 1-inch (25.4 mm) thickness of masonry or concrete.

Overlap with Florida Specific – Structural  TAC

R316.5.3 [was 314.5.3] Attics. Change to read as follows:

FBC

R316.5.3 Attics. Where attic access is required by Section R807.1 and where entry is made only for service of utilities, foam plastics shall be protected against ignition by 1.5-inch-thick (38 mm) mineral fiber insulation, 1/4-inch-thick (6.4 mm) wood structural panels, 3/8-inch (9.5 mm) particleboard, 1/4-inch (6.4 mm) hardboard, 3/8-inch (9.5 mm) gypsum board, or corrosion-resistant steel having a base metal thickness of 0.016 inch (0.406 mm) and the thermal barrier specified in Section R316.4 is not required. The ignition barrier is not required where the foam plastic insulation has been tested in accordance with Section R316.6.

IRC ’09 is changed as shown. Resolve potential conflicts.

R316.5.3 Attics. The thermal barrier specified in Section R316.4 is not required where all of the following apply:

1. Attic access is required by Section R807.1.

2. The space is entered only for purposes of repairs or maintenance.

3. The foam plastic insulation is protected against ignition using one of the following ignition barrier materials:

3.1. 11/2-inch-thick (38 mm) mineral fiber insulation;

3.2. 1/4-inch-thick (6.4 mm) wood structural panels;

3.3. 3/8-inch (9.5 mm) particleboard;

3.4. 1/4-inch (6.4 mm) hardboard;

3.5. 3/8-inch (9.5 mm) gypsum board; or

3.6. Corrosion-resistant steel having a base metal thickness of 0.016 inch (0.406 mm).

The above ignition barrier is not required where the foam plastic insulation has been tested in accordance with Section R316.6.

Staff recommendation:  IRC09 covers the Florida specific provisions.  Recommend using the IRC09 provisions instead of Florida specific provisions as stated above.

Overlap with Florida Specific – Structural TAC

R316.5.4 [was 314.5.4] Crawl spaces. Change to read as follows:

FBC

R316.5.4 Crawl spaces. Where crawlspace access is required by Section R408.3 and where entry is made only for service of utilities, foam plastics shall be protected against ignition by 1.5-inch-thick (38 mm) mineral fiber insulation, 1/4-inch-thick (6.4 mm) wood structural panels, 3/8-inch (9.5 mm) particleboard, 1/4-inch (6.4 mm) hardboard, 3/8-inch (9.5 mm) gypsum board, or corrosion-resistant steel having a base metal thickness of 0.016 inch (0.406 mm) and the thermal barrier specified in Section  316.4 is not required. The ignition barrier is not required where the foam plastic insulation n has been tested in accordance with Section R316.6.

IRC ’09 is changed as follows. Resolve potential conflicts.

R316.5.4 Crawl spaces. The thermal barrier specified in Section R316.4 is not required where all of the following apply:

1. Crawlspace access is required by Section R408.4

2. Entry is made only for purposes of repairs or maintenance.

3. The foam plastic insulation is protected against ignition using one of the following ignition barrier materials:

3.1. 11/2-inch-thick (38 mm) mineral fiber insulation;

3.2. 1/4-inch-thick (6.4 mm) wood structural panels;

3.3. 3/8-inch (9.5 mm) particleboard;

3.4. 1/4-inch (6.4 mm) hardboard;

3.5. 3/8-inch (9.5 mm) gypsum board; or

3.6. Corrosion-resistant steel having a base metal thickness of 0.016 inch (0.406 mm).

The above ignition barrier is not required where the foam plastic insulation has been tested in accordance with Section R316.6.

Staff recommendation:  The IRC09 covers Florida specific provisions.  Recommend using the IRC09 provisions instead of the Florida specific provisions as stated above.

R316.5.7 [was 314.5.7] Siding backer board. Change to read as follows:

R316.5.7 Siding backer board. Foam plastic insulation with a maximum thickness of 0.5 inch (12.7 mm) and a potential heat of not more than  2000 BTU per square foot (22 720 kJ/m2) when tested in accordance with NFPA 259 shall be permitted as siding backer board  without the thermal barrier specified in Section  R316.4 provided the foam plastic insulation is separated from interior spaces by not less than 2 inches (51 mm) of mineral fiber insulation or 1/2-inch (12.7 mm) gypsum wallboard or installed over existing exterior wall finish in conjunction with re-siding.

R316.5.9 [was 314.5.8] Interior trim. Change to read as follows:

R316.5.9 Interior trim. Exposed foam plastic trim defined as picture molds, chair rails, baseboards, handrails, ceiling beams, door trim and window trim shall be permitted, provided

1. The minimum density is 20 pounds per cubic foot (3.14 kg/m3).

2. The maximum thickness of the trim is 0.5 inch (12.7 mm) and the maximum width is 4 inches (102 mm).

3. The trim constitutes no more than 10 percent of the area of any wall or ceiling.

4. The flame-spread index does not exceed 75 when tested per ASTM E 84. The smoke-developed index is not limited.

R316.5.12 [was 314.5.12] Sheathing. Change to read as follows:

R316.5.12 Sheathing. Foam plastic insulation used as sheathing, as referenced in Table R703.4, shall comply with Sections R316.3 and Section R316.4. Where the foam plastic sheathing is used at a gable and is exposed to the attic space, the provisions of Section R316.5.3 shall apply.

Overlap with Florida Specific – Structural  TAC

R316.6 [was 314.6] Specific approval. Change to read as follows:

FBC

R316.6 Specific approval. Plastic foam not meeting the requirements of Sections R314.3 through R314.5 shall be specifically approved on the basis of one of the following approved tests: FM4880, UL 1040, NFPA 286, or UL 1715, or fire tests related to actual end-use configurations. The specific approval shall be based on the actual end use configuration and shall be performed on the finished foam plastic assembly in the maximum thickness intended for use. Assemblies tested shall include seams, joints and other typical details used in the installation of the assembly and shall be tested in the manner intended for use.

IRC ’09 is changed as follows. Resolve potential conflict.

R316.6 Specific approval. Foam plastic not meeting the requirements of Sections R316.3 through R316.5 shall be specifically approved on the basis of one of the following approved tests: NFPA 286 with the acceptance criteria of Section R302.9.4, FM 4880, UL 723, UL 1040 or UL 1715, or fire tests related to actual end-use configurations. The specific approval shall be based on the actual end use configuration and shall be performed on the finished foam plastic assembly in the maximum thickness intended for use. Assemblies tested shall include seams, joints and other typical details used in the installation of the assembly and shall be tested in the manner intended for use.

Staff recommendation:  The IRC09 covers Florida specific provisions.  Recommend using the IRC09 provisions instead of the Florida specific provisions as stated above.

Overlap with Florida Specific  - Structural TAC

Section R317.3 [was 319.3] Fasteners.  Change to read as shown.

FBC

R317.3 Fasteners. Fasteners for pressure-preservative and fire-retardant-treated wood shall be in accordance with Section R317.3.1 through R317.3.4

IRC ’09 has been changed as inserted in red. Resolve potential conflicts.

R317.3 Fasteners and connectors in contact with preservative-treated and fire-retardant-treated wood. Fasteners and connectors in contact with preservative-treated wood and fire-retardant-treated wood shall be in accordance with this section. The coating weights for zinc-coated fasteners shall be in accordance with ASTM A 153.

R317.3.1  Fasteners for Preservative Treated Wood.  Fasteners for preservative-treated wood shall be of hot-dipped zinc-coated galvanized steel, stainless steel, silicon bronze or copper. The coating weights for zinc-coated fasteners shall be in accordance with ASTM A 153.

Exceptions:

1. One-half-inch (12.7 mm) diameter or larger steel bolts.

2. Fasteners other than nails and timber rivets shall be permitted to be of mechanically deposited zinc coated steel with coating weights in accordance with ASTM B 695, Class 55, minimum.

IRC ’09 is changed as follows. Resolve potential conflicts.

R317.3.1 Fasteners for preservative-treated wood. Fasteners for preservative-treated wood shall be of hot dipped zinc-coated galvanized steel, stainless steel, silicon bronze or copper. Coating types and weights for connectors in contact with preservative-treated wood shall be in accordance with the connector manufacturer’s recommendations. In the absence of  manufacturer’s recommendations, a minimum of ASTM A 653 type G185 zinc-coated galvanized steel, or equivalent, shall be used.

Exceptions:

1. One-half-inch (12.7 mm) diameter or greater steel bolts.

2. Fasteners other than nails and timber rivets shall be permitted to be of mechanically deposited zinc coated steel with coating weights in accordance with ASTM B 695, Class 55 minimum.

Staff recommendation:  The IRC09 covers Florida specific provisions.  Recommend using the IRC09 provisions instead of the Florida specific provisions as stated above.

Overlap with Florida Specific – Structural TAC

FBC

R317.3.2 Fastenings for wood foundations.  Fastenings for wood foundations shall be as required in AF&PA Technical Report No. 7.

IRC ’09 is changed as follows to read the same as FL R319.3.2.

R317.3.2 Fastenings for wood foundations. Fastenings for wood foundations shall be as required in AF&PA Technical Report No. 7.

R317.3.3 Fasteners for fire-retardant-treated wood used in exterior applications or wet or damp locations.  Fasteners for fire-retardant-treated wood used in exterior applications or wet or damp locations shall be of hot-dipped zinc-coated galvanized steel, stainless steel, silicon bronze or copper.  Fasteners other than nails, timber rivets, wood screws and lag screws shall be permitted to be of mechanically deposited zinc coated steel with coating weights in accordance with ASTM B695, Class 55 minimum.

IRC ’09 is changed to read almost the same as FL R319.3.2 language. Resolve potential conflicts.

R317.3.3 Fasteners for fire-retardant-treated wood used in exterior applications or wet or damp locations. Fasteners for fire-retardant-treated wood used in exterior applications or wet or damp locations shall be of hot-dipped zinc-coated galvanized steel, stainless steel, silicon bronze or copper. Fasteners other than nails and timber rivets shall be permitted to be of mechanically deposited zinc-coated steel with coating weights in accordance with ASTM B 695, Class 55 minimum.

Staff recommendation:  The IRC09 covers Florida specific provisions.  Recommend using the IRC09 provisions instead of the Florida specific provisions as stated above.

Overlap with Florida Specific -  Structural TAC

FBC

R317.3.4  Fasteners for fire-retardant-treated wood used in interior applications.  Fasteners for fire-retardant-treated wood used in interior locations shall be in accordance with the manufacturer’s recommendations.  In the absence of manufacturer’s recommendations Section R317.3.3 shall apply.

IRC ’09 is changed to read the same as the FL R 319 section.

R317.3.4 Fasteners for fire-retardant-treated wood used in interior applications. Fasteners for fire-retardant-treated wood used in interior locations shall be in accordance with the manufacturer’s recommendations. In the absence of the manufacturer’s recommendations, Section R317.3.3 shall apply.

Staff recommendation:  The IRC09 covers Florida specific provisions.  Recommend using the IRC09 provisions instead of the Florida specific provisions as stated above.

R318  [was 320] Change to read as follows:

## SECTION R318

## PROTECTION AGAINST TERMITES

R318.1 Termite Protection. Termite protection shall be provided by registered termiticides, including soil applied pesticides, baiting systems, and pesticides applied to wood, or other approved methods of termite protection labeled for use as a preventative treatment to new construction. See §202, REGISTERED TERMITICIDE. Upon completion of the application of the termite protective treatment, a Certificate of Compliance shall be issued to the building department

by the licensed pest control company that contains the following statement: "The building has received a complete treatment for the prevention of subterranean termites. Treatment is in accordance with rules and laws established by the Florida Department of Agriculture and Consumer Services."

R318.1.1 If soil treatment used for subterranean termite prevention, the initial chemical soil treatment inside the foundation perimeter shall be done after all excavation, backfilling and compaction is complete.

R318.1.2If soil treatment is used for subterranean termite prevention, soil area disturbed after initial chemical soil treatment shall be retreated with a chemical soil treatment, including spaces boxed or formed.

R318.1.3 If soil treatment is used for subterranean termite prevention, space in concrete floors boxed out or formed for the subsequent installation of plumbing traps, drains or any other purpose shall be created by using plastic or metal permanently placed forms of sufficient depth to eliminate any planned soil disturbance after initial chemical soil treatment.

R318.1.4 If soil treatment is used for subterranean termite prevention, chemically treated soil shall be protected with a minimum 6 mil vapor retarder to protect against rainfall dilution. If rainfall occurs before vapor retarder placement, retreatment is required. Any work, including placement of reinforcing steel, done after chemical treatment until the concrete floor is poured, shall be done in such manner as to avoid penetrating or disturbing treated soil.

R318.1.5 If soil treatment is used for subterranean termite prevention, concrete overpour or mortar accumulated along the exterior foundation perimeter shall be removed prior to exterior chemical soil treatment, to enhance vertical penetration of the chemicals.

R318.1.6 If soil treatment is used for subterranean termite prevention, chemical soil treatments shall also be applied under all exterior concrete or grade within 1 foot (305 mm) of the primary structure sidewalls. Also, a vertical chemical barrier shall be applied promptly after construction is completed, including initial landscaping and irrigation/sprinkler installation. Any soil disturbed after the chemical vertical barrier is applied shall be promptly retreated.

R318.1.7 If a registered termiticide formulated and registered as a bait system is used for subterranean termite prevention, §1816.1.1 through §1816.1.6 do not apply; however, a signed contract assuring the installation, maintenance and monitoring of the baiting system for a  minimum of five years from the issue of the Certificate of Occupancy shall be provided to the building official prior to the pouring of the slab, and the system must be installed prior to final building approval.

If the baiting system directions for use require a monitoring phase prior to installation of the pesticide active ingredient, the installation of the monitoring phase components shall be deemed to constitute installation of the system.

R318.1.8 If a registered termiticide formulated and registered as a wood treatment is used for subterranean termite prevention, Sections R318.1.1 through R318.1.6 do not apply. Application of the wood treatment termiticide shall be as required by label directions for use, and must be completed prior to final building approval.

R318.2 Penetration. Protective sleeves around piping penetrating concrete slab-on-grade floors shall not be of cellulose-containing materials. If soil treatment is used for subterranean termite protection, the sleeve shall have a maximum wall thickness of 0.010 inch, and be sealed within the slab using a non-corrosive clamping device to eliminate the annular space between the pipe and the sleeve. No termiticides shall be applied inside the sleeve.

R318.3 Cleaning. Cells and cavities in masonry units and air gaps between brick, stone or masonry veneers and the structure shall be cleaned of all non-preservative treated or non-naturally durable wood, or other cellulose-containing material prior to concrete placement.

Exception:  Inorganic material manufactured for closing cells in foundation concrete masonry unit construction or clean earth fill placed in concrete masonry unit voids below slab level before termite treatment is performed.

R318.4 Concrete bearing ledge. Brick, stone or other veneer shall be supported by a concrete bearing ledge at least equal to the total thickness of the brick, stone or other veneer which is poured integrally with the concrete foundation. No supplemental concrete foundation pours which will create a hidden cold joint shall be used without supplemental treatment in the foundation unless there is an approved physical barrier. An approved physical barrier shall also be installed from below the wall sill plate or first block course horizontally to embed in a mortar joint. If masonry veneer extends below grade, a termite protective treatment must be applied to the cavity created between the veneer and the foundation, in lieu of a physical barrier.

Exception: Veneer supported by a structural member secured to the foundation sidewall in accordance with ACI 530/ASCE 5/TMS 402, provided at least a 6 inch (152 mm) clear inspection space of the foundation sidewall exterior exist between the veneer and the top of any soil, sod, mulch or other organic landscaping component, deck, apron, porch, walk or any other work immediately adjacent to or adjoining the structure.

R318.5.4 Foam plastic protection. Extruded and expanded polystyrene, polyisocyanurate and other foam plastics shall not be installed on the exterior face or under interior or exterior foundation walls or slab foundations located below grade.  The clearance between foam plastics installed above grade and exposed earth shall be at least 6 inches (152 mm).

Exceptions:

1. Buildings where the structural members of walls, floors, ceilings and roofs are entirely of noncombustible materials or pressure-preservative-treated wood.

2. When in addition to the requirements of Section R320.1, an approved method of protecting the foam plastic and structure from subterranean termite damage is used.

3. On the interior side of basement walls.

Section R318.6 [was R320.7] Protection against decay and termites, add text to read as follows:

R318.6 Protection against decay and termites. Condensate Lines, irrigation/sprinkler system risers for spray heads, and roof downspouts shall discharge at least 1 foot (305 mm) away from the structure sidewall, whether by underground piping, tail extensions or splash blocks. Gutters with downspouts are required on all buildings with eaves of less than 6 inches (152 mm) horizontal projection except for gable end rakes or on a roof above another roof.

R318.7 Preparation of building site and removal of debris.

R318.7.1 All building sites shall be graded to provide drainage under all portions of the building not occupied by basements.

R318.7.2 The foundation and the area encompassed within 1 foot (305 mm) therein shall have all vegetation, stumps, dead roots, cardboard, trash and foreign material removed and the fill material shall be free of vegetation and foreign material. The fill shall be compacted to assure adequate support of the foundation.

R318.7.3 After all work is completed, loose wood and debris shall be completely removed from under the building and within 1 foot (305 mm) thereof. All wood forms and supports shall be completely removed. This includes, but is not limited to: wooden grade stakes, forms, contraction spacers, tub trap boxes, plumbing supports, bracing, shoring, forms or other cellulose-containing material placed in any location where such materials are not clearly visible and readily removable prior to completion of the work.  Wood shall not be stored in contact with the ground under any building.

R320.1 [was 322.1] Change to read as shown:

SECTION R320

ACCESSIBILITY

R320.1 Scope. Shall be in accordance with the provisions of Chapter 11 of the Florida Building Code, Building.

R320.1.1 All new single-family houses, duplexes, triplexes, condominiums and townhouses shall provide at least one bathroom, located with maximum possible privacy, where bathrooms are provided on habitable grade levels, with a door that has a 29-inch (737 mm) clear opening. However, if only a toilet room is provided at grade level, such toilet rooms shall have a clear opening of not less than 29 inches (737 mm).

Section R321 [was R326 FL]  Elevators and Platform Lifts, revise text to read as follows:

SECTION R321 [was FL 326, IECC ’06 323]

ELEVATORS AND PLATFORM LIFTS

Section R321.3 Accessibility, revise text to read as follows:

R321.3 Accessibility. Reserved.

R322 [was 323] Change to read as shown:

SECTION R322

FLOOD-RESISTANT CONSTRUCTION

Add R322.4 Structural seaward of  a coastal construction line, to read as follows:

R322.4 Structures seaward of a coastal construction line. Structures located seaward of the coastal construction line shall be designed to resist the predicted forces of a 100-year storm event in accordance with Section 3109 of the Florida Building Code, Building.

R324 Add new section to read as shown:

SECTION R3245

AIRPORT NOISE

R3245.1  Airport noise study guidelines. The Aviation Safety and Noise Abatement Act of 1979, 14 CFR Part 150 (U.S. Department of Transportation), including revisions through January, 2005, are hereby adopted as a guideline for establishing airport noise control.

CHAPTER 4:  FOUNDATIONS

Section R401.1 Application, revise text to read as follows:

R401.1 Application.  R401.1 Application. The provisions of this chapter shall control the design and construction of the foundation and foundation spaces for all buildings. In addition to the provisions of this chapter, the design and construction of foundations in areas prone to flooding as established by Table R301.2(1) shall meet the provisions of Section R322. Wood foundations shall be designed and installed in accordance with AF&PA PWF.

(see Section R301.2.1.1).

Exceptions:

1.	The provisions of this chapter shall be permitted to be used for wood foundations subject to the following:

1.1. Buildings shall have no more than two floors and a roof.

1.2. Interior basement and foundation walls shall be provided at intervals not exceeding 50 feet.

1.3  When the foundation uplift loads determined from Table R401.1 exceed 0 or when such uplift loads cannot be determined from Table R401.1, an engineered design shall be required.

2.	In addition to the provisions of this chapter, the design and construction of foundations in areas prone to flooding shall meet the provisions of Section R323.

3.	Buildings and structures located within the High-Velocity Hurricane Zone shall comply with the provisions of Chapter 44.

Add Tables R401.1 to read as shown (see the 2007 Florida Building Code, Residential):

TABLE R401.1

FOUNDATION UPLIFT LIGHT STEEL & WOOD FRAME BUILDINGS IN EXPOSURE B (plf)5, 6

| Roof Angle |  | Bldg Width | Minimum Building Length | WIND VELOCITY / VELOCITY PRESSURE |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | 100 | 110 | 120 | 130 | 140 | 150 |
|  |  |  |  | 15 | 18 | 22 | 26 | 30 | 34 |
| 45 | 3 Stories3 | 20 | 12 | 173 | 276 | 389 | 512 | 644 | 787 |
|  |  | 25 | 14 | 73 | 165 | 265 | 374 | 492 | 618 |
|  |  | 30 | 19 | 0 | 81 | 174 | 275 | 384 | 502 |
|  |  | 35 | 25 | 17 | 48 | 104 | 200 | 305 | 417 |
|  |  | 40 | 35 | 33 | 69 | 109 | 152 | 240 | 349 |
|  | 2 Stories2 | 20 | 12 | 64 | 126 | 195 | 270 | 350 | 437 |
|  |  | 25 | 15 | 17 | 66 | 129 | 198 | 272 | 352 |
|  |  | 30 | 22 | 38 | 62 | 90 | 146 | 217 | 294 |
|  |  | 35 | 35 | 56 | 86 | 118 | 154 | 192 | 252 |
|  |  | 40 | 40 | 74 | 108 | 146 | 186 | 230 | 277 |
|  | 1 Story1 | 20 | 12 | 33 | 46 | 61 | 94 | 132 | 173 |
|  |  | 25 | 22 | 57 | 75 | 96 | 118 | 142 | 167 |
|  |  | 30 | 18 | 79 | 103 | 129 | 157 | 187 | 219 |
|  |  | 35 | 16 | 100 | 128 | 159 | 192 | 229 | 267 |
|  |  | 40 | 16 | 120 | 152 | 188 | 226 | 268 | 312 |
| 30 | 3 Stories3 | 20 | 12 | 92 | 177 | 271 | 373 | 483 | 601 |
|  |  | 25 | 17 | 0 | 63 | 143 | 230 | 324 | 425 |
|  |  | 30 | 25 | 0 | 23 | 52 | 125 | 209 | 300 |
|  |  | 35 | 35 | 13 | 44 | 78 | 115 | 154 | 206 |
|  |  | 40 | 40 | 28 | 64 | 102 | 145 | 190 | 239 |
|  | 2 Stories2 | 20 | 13 | 1 | 50 | 103 | 162 | 224 | 292 |
|  |  | 25 | 23 | 16 | 35 | 57 | 84 | 139 | 199 |
|  |  | 30 | 30 | 36 | 60 | 87 | 116 | 148 | 181 |
|  |  | 35 | 35 | 54 | 83 | 115 | 150 | 187 | 227 |
|  |  | 40 | 36 | 71 | 104 | 141 | 181 | 224 | 270 |
|  | 1 Story1 | 20 | 20 | 32 | 46 | 60 | 76 | 93 | 112 |
|  |  | 25 | 15 | 56 | 74 | 95 | 117 | 140 | 166 |
|  |  | 30 | 13 | 78 | 102 | 127 | 155 | 185 | 217 |
|  |  | 35 | 14 | 99 | 127 | 157 | 190 | 226 | 264 |
|  |  | 40 | 16 | 118 | 150 | 185 | 223 | 264 | 308 |

| TABLE R401.1 (continued) FOUNDATION UPLIFT LIGHT STEEL & WOOD FRAME BUILDINGS IN EXPOSURE B (plf)5, 6 |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Roof Angle |  | Bldg Width | Minimum Building Length4 | WIND VELOCITY / VELOCITY PRESSURE |  |  |  |  |  |
|  |  |  |  | 100 | 110 | 120 | 130 | 140 | 150 |
|  |  |  |  | 15 | 18 | 22 | 26 | 30 | 34 |
| 20 | 3 Stories3 | 20 | 12 | 113 | 203 | 301 | 408 | 523 | 647 |
|  |  | 25 | 14 | 45 | 130 | 222 | 322 | 431 | 547 |
|  |  | 30 | 17 | 4 | 85 | 177 | 277 | 385 | 501 |
|  |  | 35 | 19 | 20 | 58 | 154 | 257 | 369 | 489 |
|  |  | 40 | 21 | 35 | 72 | 141 | 249 | 367 | 493 |
|  | 2 Stories2 | 20 | 12 | 43 | 100 | 163 | 231 | 304 | 384 |
|  |  | 25 | 13 | 22 | 79 | 143 | 214 | 289 | 371 |
|  |  | 30 | 15 | 42 | 72 | 141 | 217 | 298 | 386 |
|  |  | 35 | 15 | 61 | 92 | 150 | 232 | 321 | 417 |
|  |  | 40 | 16 | 78 | 114 | 164 | 254 | 352 | 457 |
|  | 1 Story1 | 20 | 12 | 38 | 57 | 94 | 135 | 179 | 226 |
|  |  | 25 | 12 | 62 | 82 | 122 | 171 | 223 | 280 |
|  |  | 30 | 12 | 85 | 110 | 154 | 212 | 275 | 342 |
|  |  | 35 | 14 | 107 | 136 | 190 | 257 | 330 | 409 |
|  |  | 40 | 16 | 126 | 160 | 227 | 304 | 388 | 478 |

TABLE R401.1

FOUNDATION UPLIFT LIGHT STEEL & WOOD FRAME BUILDINGS IN EXPOSURE C (plf)5, 6

| Rf Angle |  | Bldg Width | Minimum Building Length4 | WIND VELOCITY / VELOCITY PRESSURE |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | 100 | 110 | 120 | 130 | 140 | 150 |
|  |  |  |  | 21 | 26 | 31 | 36 | 42 | 48 |
| 45 | 3 Stories3 | 20 | 12 | 370 | 515 | 673 | 845 | 1031 | 1231 |
|  |  | 25 | 13 | 249 | 377 | 518 | 670 | 836 | 1013 |
|  |  | 30 | 17 | 159 | 278 | 408 | 550 | 703 | 867 |
|  |  | 35 | 21 | 89 | 203 | 328 | 463 | 610 | 767 |
|  |  | 40 | 26 | 102 | 153 | 262 | 394 | 537 | 691 |
|  | 2 Stories2 | 20 | 12 | 184 | 271 | 368 | 472 | 585 | 706 |
|  |  | 25 | 13 | 119 | 200 | 288 | 385 | 489 | 601 |
|  |  | 30 | 18 | 85 | 147 | 233 | 326 | 426 | 533 |
|  |  | 35 | 24 | 113 | 155 | 200 | 284 | 383 | 489 |
|  |  | 40 | 36 | 139 | 187 | 240 | 297 | 358 | 457 |
|  | 1 Story1 | 20 | 12 | 58 | 95 | 140 | 189 | 243 | 300 |
|  |  | 25 | 16 | 92 | 118 | 147 | 178 | 224 | 281 |
|  |  | 30 | 19 | 124 | 157 | 193 | 233 | 275 | 321 |
|  |  | 35 | 17 | 154 | 193 | 236 | 283 | 334 | 388 |
|  |  | 40 | 16 | 182 | 227 | 277 | 331 | 389 | 452 |
| 30 | 3 Stories3 | 20 | 12 | 256 | 376 | 507 | 650 | 804 | 970 |
|  |  | 25 | 15 | 130 | 232 | 344 | 466 | 598 | 740 |
|  |  | 30 | 21 | 47 | 127 | 228 | 337 | 455 | 582 |
|  |  | 35 | 31 | 72 | 116 | 163 | 241 | 351 | 469 |
|  |  | 40 | 40 | 96 | 146 | 200 | 259 | 323 | 392 |
|  | 2 Stories2 | 20 | 12 | 95 | 163 | 238 | 320 | 408 | 502 |
|  |  | 25 | 18 | 53 | 85 | 151 | 223 | 301 | 385 |
|  |  | 30 | 30 | 83 | 117 | 154 | 195 | 239 | 304 |
|  |  | 35 | 35 | 110 | 150 | 195 | 244 | 296 | 353 |
|  |  | 40 | 37 | 135 | 182 | 233 | 289 | 350 | 415 |
|  | 1 Story1 | 20 | 20 | 58 | 76 | 97 | 119 | 143 | 169 |
|  |  | 25 | 16 | 91 | 117 | 145 | 176 | 210 | 245 |
|  |  | 30 | 13 | 123 | 156 | 191 | 230 | 272 | 317 |
|  |  | 35 | 14 | 152 | 191 | 234 | 280 | 330 | 384 |
|  |  | 40 | 16 | 179 | 224 | 273 | 327 | 384 | 446 |

| TABLE R401.1(continued) FOUNDATION UPLIFT LIGHT STEEL & WOOD FRAME BUILDINGS IN EXPOSURE C (plf)5, 6 |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Rf Angle |  | Bldg Width | Minimum Building Length4 | WIND VELOCITY / VELOCITY PRESSURE |  |  |  |  |  |
|  |  |  |  | 100 | 110 | 120 | 130 | 140 | 150 |
|  |  |  |  | 21 | 26 | 31 | 36 | 42 | 48 |
| 20 | 3 Stories3 | 20 | 12 | 285 | 411 | 549 | 698 | 860 | 1034 |
|  |  | 25 | 13 | 207 | 325 | 455 | 595 | 748 | 911 |
|  |  | 30 | 15 | 162 | 280 | 409 | 549 | 701 | 863 |
|  |  | 35 | 17 | 138 | 260 | 393 | 538 | 695 | 863 |
|  |  | 40 | 18 | 124 | 252 | 392 | 545 | 709 | 886 |
|  | 2 Stories2 | 20 | 12 | 152 | 233 | 320 | 416 | 519 | 630 |
|  |  | 25 | 12 | 133 | 215 | 306 | 404 | 511 | 625 |
|  |  | 30 | 13 | 130 | 219 | 316 | 422 | 536 | 658 |
|  |  | 35 | 14 | 138 | 235 | 341 | 456 | 581 | 715 |
|  |  | 40 | 16 | 150 | 257 | 373 | 500 | 636 | 783 |
|  | 1 Story1 | 20 | 12 | 88 | 136 | 188 | 245 | 307 | 373 |
|  |  | 25 | 12 | 114 | 172 | 235 | 303 | 377 | 457 |
|  |  | 30 | 12 | 146 | 214 | 288 | 370 | 457 | 552 |
|  |  | 35 | 14 | 180 | 259 | 346 | 441 | 543 | 653 |
|  |  | 40 | 16 | 215 | 306 | 406 | 515 | 632 | 758 |

Notes:

- Based on 1st floor height = 10 ft. or 11 ft. floor to floor in multi-story.

- Based on 2nd floor height = 8 ft. or 9 ft. floor to floor in multi-story.

- Based on 3rd floor height = 8 ft.

- Building length shall be equal to or greater than that shown in tables.

- Roof and floor framing shall span in the same direction.

- Includes provision for 2 foot roof overhang

Change Figures to Florida-specific figures (see the 2007 Florida Building Code):

Figure R403.1(1)  Concrete and Masonry Foundation Details.

FOOTING A

MONOLITHIC SLAB ON GRADE EXTERIOR WALL

FOOTING B

MONOLITHIC SLAB ON GRADE INTERIOR WALL

FOOTING C

STEM WALL WOOD JOIST FLOOR

Footing D

Monolithic Exterior Footing

Footing E

Monolithic Interior Footing

Footing F

Wood Floor to Concrete or Masonry Stemwall

Footing G

Stemwall Foundation with Slab-on-Grade

FOOTING H

R401.2, Requirements. Change to read as shown:

R401.2 Requirements. Foundations shall be capable of resisting all loads from roof uplift and building overturn. Foundation uplift for light-frame wood or steel buildings shall be calculated or determined from Table R401.1. Masonry buildings within the dimensional scope of Table R401.1 shall be assumed to be of adequate weight so as not to require uplift resistance greater than that provided by the structure and any normal foundation.   Foundation construction shall also be capable of accommodating all gravity loads according to Section R301 and of transmitting the resulting loads to the supporting soil. Fill soils that support footings and foundations shall be designed, installed and tested in accordance with accepted engineering practice. Gravel fill used as footings for wood and precast concrete foundations shall comply with Section R403.

Table R402.2 Minimum Specified Compressive Strength of Concrete, revise footnote “b”  to read as follows:

a. No change

b.  See Table R301.2(3) for weathering potential.

c-f No change.

Overlap with Florida Specific – Structural TAC

FBC

R403.1.1 Change to read as shown:

R403.1.1 Minimum size. Minimum sizes for concrete and masonry footings shall be as set forth in Table R403.1 and Figure R403.1(1). Minimum sizes for concrete and masonry footings shall also be as required to provide adequate resistance to uplift and overturn of the building as determined from Table 401.1 or as calculated using engineered design in accordance with the Florida Building Code, Building. The footing width, W, shall be based on the load-bearing value of the soil in accordance with Table R401.4.1. Spread footings shall be at least 8 inches (152 mm) in thickness. Footing projections, P, shall be at least 2 inches (51 mm) and shall not exceed the thickness of the footing. The size of footings supporting piers and columns shall be based on the tributary load and allowable soil pressure in accordance with Table R401.4.1. Footings for wood foundations shall be in accordance with the details set forth in Section R403.2, and Figures R403.1(2) and R403.1(3).

IRC ’09 has been changed as shown. Resolve potential conflicts.

R403.1.1 Minimum size. Minimum sizes for concrete and masonry footings shall be as set forth in Table R403.1 and Figure R403.1(1). The footing width, W, shall be based on the load-bearing value of the soil in accordance with Table R401.4.1. Spread footings shall be at least 6 inches (152 mm) in thickness, T. Footing projections, P, shall be at least 2 inches (51 mm) and shall not exceed the thickness of the footing. The size of footings supporting piers and columns shall be based on the tributary load and allowable soil pressure in accordance with Table R401.4.1. Footings for wood foundations shall be in accordance with the details set forth in Section R403.2, and Figures R403.1(2) and R403.1(3).

Staff recommendation:  The IRC09 does not cover Florida specific provisions.  Recommend retaining Florida specific provisions as stated above.

R403.1.2 Add to read as shown:

R403.1.2 Resistance to uplift. Uplift resistance of common foundations are given in Table R403.1.21. Uplift resistance of these foundations may be increased by increasing the size of the concrete footing. When determining the modified uplift resistance the added weight shall be reduced by multiplying by a factor of 0.6. Other foundation systems shall be engineered in accordance with the Florida Building Code, Building.

TABLE R403.1.21

FOUNDATION UPLIFT DESIGN DETAILS

| FOOTING | TYPE | T | W | SLAB/WALL1 | RESISTANCE | NOTES |
| --- | --- | --- | --- | --- | --- | --- |
| A | Mono | 20 | 12 | 6 | 502 | 3 |
|  | Mono | 20 | 16 | 6 | 285 | 3 |
| B | Mono Interior | 20 | 12 | 13 | 796 | 3 |
|  | Mono Interior | 20 | 16 | 13 | 879 | 3 |
| C | 12” Stem/Joist | 10 | 20 | 228 | 436 | 1,2,3 |
| D | Mono | 20 | 12 | 6 | 502 | -- |
|  | Mono | 20 | 16 | 6 | 585 | -- |
| E | Mono Interior | 20 | 12 | 13 | 796 | -- |
|  | Mono Interior | 20 | 16 | 13 | 879 | -- |
| F | Stem/Joist | 10 | 20 | -- | 208 | 2,3 |
| G | Stem/Slab | 10 | 20 | 6 | 460 | 3 |
| H | Stem/Slab | 10 | 12 | 6 | 377 | 3 |
|  | Stem/Slab | 10 | 20 | 6 | 460 | 3 |

For SI: 1 inch = 25.4 mm.

1. Tributory width of 3½" slab or weight of stemwall and bond beam

2. 1st floor dead load multiplied by 0.6 may also be included.

3. All footing dowel bars shall be same size as wall steel, shall have a standard 90-degree hook, and shall be embedded a minimum of 6 inches. Dowel bars shall lap vertical wall reinforcement a minimum of 25 inches.

R403.1.3 Change to read as shown:

R403.1.3 Seismic reinforcing. Reserved.

R403.1.4 Change to read as shown:

R403.1.4 Minimum depth.  All exterior footings shall be placed at least 12 inches (305 mm) below the undisturbed ground surface. Where applicable…through R403.1.4.2.

R403.1.4.1 Frost protection. Reserved.

R403.1.4.2 Seismic conditions. Reserved.

R403.1.6 Change to read as shown:

R403.1.6 Foundation anchorage.  Reserved.

R403.1.6.1 Foundation anchorage in Seismic Design Categories C, D0, D1 and D2. Reserved.

R403.3 Change to read as shown:

R403.3 Frost protected shallow foundations. Reserved

Figures R403.3(1) through R403.3(4)  Reserved.

Table 403.3(1) Reserved.

R403.3.1 Foundations adjoining frost protected shallow foundations. Reserved.

R403.3.1.1 Attachment to unheated slab-on-ground structure. Reserved.

R403.3.1.2 Attachment to heated structure.  Reserved.

R403.3.2 Protection of horizontal insulation below ground. Reserved.

R403.3.3 Drainage. Reserved.

R403.3.4 Termite damage. Reserved.

Overlap with Florida Specific – Structural TAC

FBC

R404.1.1 Change to read as follows

R404.1.1 Masonry foundation walls. Concrete masonry and clay masonry foundation walls shall be constructed as set forth in Tables R404.1.1(2), R404.1.1(3) and R404.1.1(4) and shall also comply with the provisions of this section and the applicable provisions of Sections R606, R607 and R608. In seismic…R404.1.4. Rubble stone masonry foundation walls shall be constructed in accordance with Sections R404.1.8 and R607.2.2. The use of rubble stone masonry foundation walls and plain masonry shall be limited to regions where the basic wind speed is 100 mph or less unless an engineered design is provided.[Delete rest of section]

IRC ’09 has been changed. Resolve potential conflicts.

R404.1.1 Design of masonry foundation walls. Masonry foundation walls shall be designed and constructed in accordance with the provisions of this section or in accordance with the provisions of ACI530/ASCE 5/TMS 402 or NCMA TR68-A. When ACI530/ASCE 5/TMS 402, NCMA TR68-A or the provisions of this section are used to design masonry foundation walls, project drawings, typical details and specifications are not required to bear the seal of the architect or engineer responsible for design, unless otherwise required by the state law of the jurisdiction having authority.

R404.1.1.1 Masonry foundation walls. Concrete masonry and clay masonry foundation walls shall be constructed as set forth in Table R404.1.1(1), R404.1.1(2), R404.1.1(3) or R404.1.1(4) and shall also comply with applicable provisions of Sections R606, R607 and R608. In buildings assigned to Seismic DesignCategoriesD0,D1 and D2, concrete masonry and clay masonry foundation walls shall also comply with Section R404.1.4.1. Rubble stone masonry foundation walls shall be constructed in accordance with Sections R404.1.8 and R607.2.2. Rubble stone masonry walls shall not be used in Seismic Design Categories D0, D1 and D2.

Staff recommendation:  The IRC09 does not cover Florida specific provisions.  Recommend retaining Florida specific provisions as stated above.

R404.1.1.1.1 Add to read as shown:

R404.1.1.1.1 Bond beams, footing dowels and foundation wall reinforcing, wood or steel light-framed first story walls. Where first story walls are of wood or steel light-frame, a minimum 8 inch x 8 inch (203 mm x 203 mm) nominal grouted masonry or concrete bond beam shall be provided at the top course of the foundation wall. The bond beam shall be reinforced with not less than one No. 5 bar, continuous around corners and intersections.

R404.1.1.1.2 Where first story walls are of wood or steel light-frame, footing dowel bars and foundation vertical reinforcing shall be not less than No. 4 bars at 8 ft (2438 mm) on center, placed in fully grouted cells. Dowels shall extend into the cast concrete footing and terminate with a standard hook at three inches clear of the footing bottom. Vertical wall reinforcing shall be lap spliced with the dowel, extend into the bond beam at the wall top, and terminate with a standard hook at 1-1/2 inches (38 mm) clear of the top of the bond beam. Alternately, stem wall vertical reinforcing shall be permitted to extend into the footing and be terminated with a standard hook at 3 inches (76 mm) clear of the bottom of the footing. In addition grouted, reinforced vertical cells shall be provided at hold down post anchorages and at uplift anchorages that use straps embedded into concrete or masonry.

Overlap with Florida Specific - Structural TAC

FBC

R404.1.2 Change to read as follows.

R404.1.2 Concrete foundation walls.  Concrete foundation walls shall be constructed as set forth in Tables R404.1.1(1), R404.1.1(2), R404.1.1(3) and R404.1.1(4), and shall also comply with the provisions of this section and the applicable provisions of Section R402.2. In seismic…with Section R404.1.4.

IRC ’09 is changed as shown. Resolve potential conflicts.

R404.1.2 Concrete foundation walls. Concrete foundation walls that support light-frame walls shall be designed and constructed in accordance with the provisions of this section, ACI 318, ACI 332 or PCA 100. Concrete foundation walls that support above-grade concrete walls that are within the applicability limits of Section R611.2 shall be designed and constructed in accordance with the provisions of this section, ACI 318, ACI 332 or PCA 100. Concrete foundation walls that support above-grade concrete walls that are not within the applicability limits of Section R611.2 shall be designed and constructed in accordance with the provisions of ACI 318, ACI 332 or PCA 100. When ACI 318, ACI 332, PCA 100 or the provisions of this section are used to design concrete foundation walls, project drawings, typical details and specifications are not required to bear the seal of the architect or engineer responsible for design, unless otherwise required by the state law of the jurisdiction having authority.

R404.1.2.1 Concrete cross-section. Concrete walls constructed in accordance with this code shall comply

with the shapes and minimum concrete cross-sectional dimensions required by Table R611.3. Other types of forming systems resulting in concrete walls not in compliance with this section and Table R611.3 shall be designed in accordance with ACI 318.

R404.1.2.2 Reinforcement for foundation walls. Concrete foundation walls shall be laterally supported at the top and bottom. Horizontal reinforcement shall be provided in accordance with TableR404.1.2(1).Vertical reinforcement shall be provided in accordance with Table R404.1.2(2), R404.1.2(3), R404.1.2(4), R404.1.2(5), R404.1.2(6), R404.1.2(7) or R404.1.2(8). Vertical reinforcement for flat basement walls retaining 4 feet (1219 mm) or more of unbalanced backfill is permitted to be determined in accordance with Table R404.1.2(9). For basement walls supporting above-grade concrete walls, vertical reinforcement shall be the greater of that required by Tables R404.1.2(2) through R404.1.2(8) or by Section R611.6 for the above-grade wall. In buildings assigned to Seismic Design Category D0, D1 or D2, concrete foundation walls shall also comply with Section R404.1.4.2.

R404.1.2.2.1 Concrete foundation stem walls supporting above-grade concrete walls. Foundation stem walls that support above-grade concrete walls shall be designed and constructed in accordance with this section.

1. Stem walls not laterally supported at top. Concrete stem walls that are not monolithic with slabs-on-ground or are not otherwise laterally supported by slabs-on-ground shall comply with this section. Where unbalanced backfill retained by the stem wall is less than or equal to 18 inches (457 mm), the stem wall and above-grade wall it supports shall be provided with vertical reinforcement in accordance with Section R611.6 and Table R611.6(1), R611.6(2) or R611.6(3) for above-grade walls. Where unbalanced backfill retained by the stem wall is greater than 18 inches (457 mm), the stem wall and above-grade wall it supports shall be provided with vertical reinforcement in accordance with Section R611.6 and Table R611.6(4). 2. Stem walls laterally supported at top. Concrete stem walls that are monolithic with slabs-on ground or are otherwise laterally supported by slabs-on-ground shall be vertically reinforced in accordance with Section R611.6 and Table R611.6(1), R611.6(2) or R611.6(3) for above grade walls. Where the unbalanced backfill retained by the stem wall is greater than 18 inches (457 mm), the connection between the stem wall and the slab-on-ground, and the portion of the slab-on-ground providing lateral support for the wall shall be designed in accordance with PCA 100 or in accordance with accepted engineering practice. Where the unbalanced backfill retained by the stem wall is greater than 18 inches (457 mm), the minimum nominal thickness of the wall shall be 6 inches (152 mm).

R404.1.2.2.2 Concrete foundation stem walls supporting light-frame above-grade walls. Concrete foundation stem walls that support light-frame above-grade walls shall be designed and constructed in accordance with this section.

1. Stem walls not laterally supported at top. Concrete stem walls that are not monolithic with slabs-on-ground or are not otherwise laterally supported by slabs-on-ground and retain 48 inches (1219 mm) or less of unbalanced fill, measured from the top of the wall, shall be constructed in accordance with Section R404.1.2. Foundation stem walls that retain more than 48 inches (1219 mm) of unbalanced fill, measured from the top of the wall, shall be designed in accordance with Sections R404.1.3 and R404.4.

2. Stem walls laterally supported at top. Concrete stem walls that are monolithic with slabs-on ground or are otherwise laterally supported by slabs-on-ground shall be constructed in accordance with Section R404.1.2. Where the unbalanced backfill retained by the stem wall is greater than 48 inches (1219 mm), the connection

between the stem wall and the slab-on- ground, and the portion of the slab-on-ground providing lateral support for the wall shall be designed in accordance with PCA 100 or in accordance with accepted engineering practice.

Staff recommendation:  The IRC09 does not cover Florida specific provisions.  Recommend retaining Florida specific provisions as stated above.

R404.1.2.3.1 Compressive strength.  Reserved.

R404.1.2.3.7.1 Steel reinforcement. Steel reinforcement shall comply with the requirements of ASTM A 615, A 706, or A 996. ASTM A 996 bars produced from rail steel shall be Type R. In buildings assigned to Seismic Design Category A, B or C, the minimum yield strength of reinforcing steel shall be 40,000 psi (Grade 40) (276MPa). In buildings assigned to Seismic Design Category D0, D1 or D2, reinforcing steel shall comply with the requirements of ASTM A 706 for low-alloy steel with a minimum yield strength of 60,000 psi (Grade 60) (414 MPa).

R404.1.2.4 Requirements for Seismic Design Category C. Reserved.

R404.2.7 [was R404.1.4] Add to read as follows:

R404.2.7 Anchorage of wood and steel light-frame wall systems. Anchorage of wood or steel light framed first story walls shall be in accordance with the following:

R404.1.4.1 For wood light-frame walls, sill plate anchorage, wall stud to foundation uplift anchorage and hold down post anchorage shall be in accordance with AF&PA WFCM

R404.1.4.2 For steel light-frame walls, wall bottom and braced wall chord stud anchorage shall be in accordance with AISI COFS/PM.

IPC ’09  has no changes to wood foundation walls; it is located in Section 404.2.

R404.1.5.3 [was 404.1.5.1] Change to read as follows:

R404.1.5.31 Pier and curtain wall foundations. In regions where the basic wind speed is 100 mph or less pier and curtain wall foundations shall be permitted to be used to support light-frame construction not more than two stories in height, provided the following requirements are met:

1-2  No change.

3.	Piers shall be constructed in accordance with Section R606.5 and Section R606.6.1,

and shall be bonded into the load-bearing masonry wall in accordance with Section R608.1.1 or Section R608.1.1.2.

4 – 6 No change.

7.  Reserved.

R404.1.8 Change to read as follows:

R404.1.8 Rubble stone masonry. Rubble stone masonry foundation walls shall have a minimum thickness of 16 inches (406 mm), shall not support an unbalanced backfill exceeding 8 feet (2438 mm) in height, and shall not support a soil pressure greater than 30 psf (481 kg/m2) and shall not be constructed in Seismic Design Categories D0, D1, D2 or townhouses in Seismic Design Category C, as established in Figure R301.2(2).

R404.2.6 Change reference to read as follows:

R404.2.6 Fastening. Wood structural panel foundation wall sheathing shall be attached to framing in accordance with Table R602.2(1) and Section R402.1.1.

Section R404.3 Wood sill plates, revise to read as follows:

R404.3 Wood sill plates. Wood sill plates shall be a minimum of 2-inch by 4-inch (51 mm by 102 mm) nominal lumber. Sill plate anchorage shall be in accordance with Sections R403.1.6 and R602.1.1.

Overlap with Florida Specific - Structural TAC

FBC

R404.4 Insulating concrete form foundation wall criteria have been deleted from Sections R404.4.1 and R404.4.7.2 and moved to Section R404.1.2.3.6.  They are rewritten as shown. Resolve potential conflicts.

R404.4.1 Applicability limits. The provisions of this section shall apply to the construction of insulating concrete form foundation walls for buildings not greater than 60 feet (18 288 mm) in plan dimensions, and floors not greater than 32 feet (9754 mm) or roofs not greater than 40 feet (12 192 mm) in clear span. Buildings shall not exceed two stories in height above-grade with each story not greater than 10 feet (3048 mm) high. Insulating concrete form foundation walls supporting above-grade concrete walls shall be reinforced as required for the above-grade wall immediately above or the requirements in Tables R404.4(1), R404.4(2), R404.4(3), R404.4(4) or R404.4(5), whichever is greater.

R404.4.7.2 Termite hazards.  In areas where hazard of termite damage is very heavy in accordance with Figure R301.2(6), Foam plastic insulation shall be permitted below grade on foundation walls in accordance with one of the following conditions:

1.	When in addition to the requirements in Section R320.1, an approved method of protecting the foam plastic and structure from subterranean termite damage is provided.

2.	The structural members of walls, floors, ceilings and roofs are entirely of noncombustible materials or pressure preservatively treated wood.

3.	On the interior side of basement walls.

R404.1.2.3.6 Form materials and form ties. Forms shall be made of wood, steel, aluminum, plastic, a composite of cement and foam insulation, a composite of cement and wood chips, or other approved material suitable for supporting and containing concrete. Forms shall provide sufficient strength to contain concrete during the concrete placement operation. Form ties shall be steel, solid plastic, foam plastic, a composite of cement and wood chips, a composite of cement and foam plastic, or other suitable material capable of resisting the forces created by fluid pressure of fresh concrete.

R404.1.2.3.6.1 Stay-in-place forms. Stay-in place concrete forms shall comply with this section.

1. Surface burning characteristics. The flame-spread index and smoke-developed index of forming material, other than foam plastic, left exposed on the interior shall comply with Section R302. The surface burning characteristics of foam plastic used in insulating concrete forms shall comply with Section R316.3.

2. Interior covering. Stay-in-place forms constructed of rigid foam plastic shall be protected on the interior of the building as required by Section R316. Where gypsum board is used to protect the foam plastic, it shall be installed with a mechanical fastening system. Use of adhesives in addition to mechanical fasteners is permitted.

3. Exterior wall covering. Stay-in-place forms constructed of rigid foam plastics shall be protected from sunlight and physical damage by the application of an approved exterior

wall covering complying with this code. Exterior surfaces of other stay-in-place forming systems shall be protected in accordance with this code.

4. Termite hazards. In areas where hazard of termite damage is very heavy in accordance with Figure R301.2(6), f Foam plastic insulation shall be permitted below grade on foundation walls in accordance with one of the following conditions:

4.1. Where in addition to the requirements in Section R318.1, an approved method of protecting the foam plastic and structure from subterranean termite damage is provided.

4.2. The structural members of walls, floors, ceilings and roofs are entirely of noncombustible materials or pressure-preservative-treated wood.

4.3. On the interior side of basement walls.

Staff recommendation:  The IRC09 does not cover Florida specific provisions.  Recommend using the IRC09 as the base text and then revise text to add Florida specific requirements as  stated above.

Revise R404.5.2 as follows:

R404.5.2 Precast concrete foundation design drawings.  Precast concrete foundation wall design drawings shall be submitted to the building official and approved prior to installation. Drawings shall include, at a minimum, the information specified below:

1. Design loading as applicable;

2. Footing design and material;

3. Concentrated loads and their points of application;

4. Soil bearing capacity;

5. Maximum allowable total uniform load; and

6. Seismic design category; and

7. Basic wind speed.

Revise R407.3 to read as follows:

R407.3 Structural requirements. The columns shall be restrained to prevent lateral displacement at the bottom end. Wood columns shall not be less in nominal size than 4 inches by

4 inches (102 mm by 102 mm). Steel columns shall not be less than 3-inch-diameter (76 mm) Schedule 40 pipe manufactured in accordance with ASTM A 53 Grade B or approved equivalent.

Exception: Reserved. In Seismic Design Categories A, B and C, columns no more than 48 inches (1219 mm) in height on a pier or footing are exempt from the bottom end lateral displacement requirement within under-floor areas enclosed by a continuous foundation.

Section R408.1 Ventilation.  Add exception to read as shown.

Exception: Crawl spaces, designed by a Florida licensed engineer or registered architect to eliminate the venting.

Overlap with Florida Specific - Structural TAC

IRC ‘09 is changed as shown. Resolve potential conflicts.

FBC

Section R408.3 Unvented crawl space, change to read as shown:

R408.3 Unvented crawl space. Ventilation openings in under-floor spaces specified in Sections R408.1 and R408.2 shall not be required where:

1. Exposed earth is covered with a continuous vapor retarder. Joints of the vapor retarder shall overlap by 6 inches (152 mm) and shall be sealed or taped. The edges of the vapor retarder shall extend at least 6 inches (152 mm) up the stem wall and shall be attached and sealed to the stem wall; and

2. One of the following is provided for the under-floor space:

2.1. Continuously operated mechanical exhaust ventilation at a rate equal to 1 cfm (0.47 L/s) for each 50 ft2 (4.7m2) of crawlspace floor area, including an air pathway to the common area (such as a duct or transfer grille), and perimeter walls insulated in accordance with Section B2.5.6 of Appendix G;

2.2. Conditioned air supply sized to deliver at a rate equal to 1 cfm (0.47 L/s) for each 50 ft2 (4.7 m2) of under-floor area, including a return air pathway to the common area (such as a duct or transfer grille), and perimeter walls insulated in accordance with Section B2.5.6 of Appendix G;

2.3. Plenum complying with Section M1601.4, if under-floor space is used as a plenum.

IRC ’09 is changed in part as shown. Resolve potential conflicts.

R408.3 Unvented crawl space. Ventilation openings in under-floor spaces specified in Sections R408.1 and R408.2 shall not be required where:

1. Exposed earth is covered with a continuous Class I vapor retarder. Joints of the vapor retarder shall overlap by 6 inches (152 mm) and shall be sealed or taped. The edges of the vapor retarder shall extend at least 6 inches (152 mm) up the stem wall and shall be attached and sealed to the stem wall; and

2. One of the following is provided for the under-floor space:

2.1. Continuously operated mechanical exhaust ventilation at a rate equal to 1 cubic foot per minute (0.47 L/s) for each 50 square feet (4.7m2) of crawlspace floor area, including an air pathway to the common area (such as a duct or transfer grille), and perimeter walls insulated in accordance with Section N1102.2.9;

2.2. Conditioned air supply sized to deliver at a rate equal to 1 cubic foot per minute (0.47 L/s) for each 50 square feet (4.7 m2) of under-floor area, including a return air pathway to the common area (such as a duct or transfer grille), and perimeter walls insulated in accordance with Section N1102.2.9;

2.3. Plenum in existing structures complying with Section M1601.5, if under-floor space is used as a plenum.

NOTE:  IRC ’09 N1102.2.9 is changed to specify Class I vapor retarders and fix sentence construction. No apparent conflict. Needs to be changed in Section B2.5.6 of Appendix G (or equivalent).

Staff recommendation:  The IRC09 does not cover Florida specific provisions.  Recommend using the IRC09 provisions as the base text and then revise text to add Florida specific provisions as stated above.

CHAPTER 5 FLOORS

R501.1 Application. Change to read as follows:

R501.1 Application. The provisions of this chapter shall control the design and construction of the floors for all buildings including the floors of attic spaces used to house mechanical and/or plumbing fixtures and equipment (see Section R301.2.1.1).

Exception: Buildings and structures located within the High-Velocity Hurricane Zone shall comply with the provisions of Chapter 44.

R502.1 Add section R502.1 as follows and renumber following sections as shown:

R502.1 General Requirements. Floor framing of light-frame wood construction shall be in accordance with the provisions of this Section.

R502.1.1  Identification. [IRC R502.1] Load-bearing dimension lumber for joists, beams and girders shall be identified by a grade mark of a lumber grading or inspection agency that has been approved by an accreditation body that complies with DOCPS 20. In lieu of a grade mark, a certificate of inspection issued by a lumber grading or inspection agency meeting the requirements of this section shall be accepted.

R502.1.1.1 Preservatively treated lumber.  [IRC R502.1.1] Preservative treated dimension lumber shall also be identified as required by Section R319.1.

R502.1.1.2 Blocking and subflooring.  [IRC R502.1.2] Blocking shall be a minimum of utility grade lumber. Subflooring may be a minimum of utility grade lumber or No. 4 common grade boards.

R502.1.1.3 End-jointed lumber.  [IRC R502.1.3] Approved end-jointed lumber identified by a grade mark conforming to Section R502.1 may be used interchangeably with solid-sawn members of the same species and grade.

R502.1.1.4 Prefabricated wood I-joists.  [IRC R502.1.4] Structural capacities and design provisions for prefabricated wood I-joists shall be established and monitored in accordance with ASTM D 5055.

R502.1.1.5 Structural glued laminated timbers. [IRC R502.1.5]

Glued laminated timbers shall be manufactured and identified as required in ANSI/AITC A190.1 and ASTM D 3737.

R502.1.1.6 Structural log members [IRC R502.1.6]. Stress grading of structural log members of nonrectangular shape, as typically used in log buildings, shall be in accordance with ASTM D 3957. Such structural log members shall be identified by the grade mark of an approved lumber grading or inspection agency. In lieu of a grade mark on the material, a certificate of inspection as to species and grade issued by a lumber-grading or inspection agency meeting the requirements of this section shall be permitted to be accepted.

R502.1.1.7 Exterior wood/plastic composite deck boards.  [IRC R502.1.7] Wood/plastic composites used in exterior deck boards shall comply with the provisions of Section R317.4.

R502.1.2 Draftstopping required. [IRC R502.12]  Draftstopping shall be provided in accordance with Section R302.12.

R502.1.2.12  Fireblocking required [IRC R502.13]. Fireblocking shall be provided in accordance with Section R302.11 R602.1.2.

R502.11, Wood trusses. Change section numbers as shown.

R502.1.3 Wood trusses [IRC R502.11].

R502.1.3.1 Design. Renumber and change to read as shown:

R502.1.3.1 Design [IRC R502.11.1].  Wood trusses shall be designed in accordance with approved engineering practice. The design and manufacture of metal plate connected wood trusses shall comply with ANSI/TPI 1. The truss design drawings shall be prepared by a registered professional where required by Florida Statutes.  the statutes of the jurisdiction in which the project is to be constructed in accordance with Section R106.1.

Section R502.1.3.2 Bracing.  Renumber and change to read as shown.

R502.1.3.2 Bracing [IRC R502.11.2]. Trusses shall be braced to prevent rotation and provide lateral stability in accordance with the requirements specified in the construction documents for the building and on the individual truss design drawings. In the absence of specific bracing requirements, trusses shall be braced in accordance with TPI/WTCA BCSI

R502.1.3.3 Alterations to trusses [IRC R502.11.3].  Truss members and components shall not be cut, notched, spliced or otherwise altered in anyway without the approval of a registered design professional. Alterations resulting in the addition of load (e.g., HVAC equipment, water heater, etc.), that exceed the design load for the truss, shall not be permitted without verification that the truss is capable of supporting the additional loading.

R502.1.3.4 Truss design drawings [IRC R502.11.4]. Truss design drawings, prepared in compliance with Section R502.1.3.1, shall be provided to the building official and approved prior to installation. Truss design drawing shall be provided with the shipment of trusses delivered to the job site. Truss design drawings shall include, at a minimum, the information specified below:

1. Slope or depth, span and spacing.

2. Location of all joints.

3. Required bearing widths.

4. Design loads as applicable:

4.1. Top chord live load;

4.2. Top chord dead load;

4.3. Bottom chord live load;

4.4. Bottom chord dead load;

4.5. Concentrated loads and their points of application; and

4.6. Controlling wind loads.

5. Adjustments to lumber and joint connector design values for conditions of use.

6. Each reaction force and direction.

7. Joint connector type and description, e.g., size, thickness or gauge, and the dimensioned location of each joint connector except where symmetrically located relative to the joint interface.

8. Lumber size, species and grade for each member.

9. Connection requirements for:

9.1. Truss-to-girder-truss;

9.2. Truss ply-to-ply; and

9.3. Field splices.

10. Calculated deflection ratio and/or maximum description for live and total load.

11. Maximum axial compression forces in the truss members to enable the building designer to design the size, connections and anchorage of the permanent continuous lateral bracing. Forces shall be shown on the truss drawing or on supplemental documents.

12. Required permanent truss member bracing location.

R502.2 Change to read as follows:

R502.2 Design and construction where wind speed is less than 100 mph.  Floors shall be designed and constructed in accordance with the provisions of this Section and Figure R502.2 and Sections R319 and R320 or in accordance with AF&PA’s NDS.

R502.2.1 Framing at braced wall lines. A load path for lateral forces shall be provided between floor framing and braced wall panels located above or below a floor, as specified in Section R602.10.8.

R502.2.2 Decks. Where supported by attachment to an exterior wall, decks shall be positively anchored to the primary structure and designed for both vertical and lateral loads as applicable. Such attachment shall not be accomplished by the use of toenails or nails subject to withdrawal.

Where positive connection to the primary building structure cannot be verified during inspection, decks shall be self supporting. For decks with cantilevered framing members, connections to exterior walls or other framing members, shall be designed and constructed to resist uplift resulting from the full live load specified in Table R301.5 acting on the cantilevered portion of the deck.

IRC ’09 additional code added here.

R502.2.3 Allowable joist spans. [IRC R502.3] Spans for floor joists shall be in accordance with Tables R502.2.3(1) and R502.2.3 (2). For other grades and species and for other loading conditions, refer to the AF&PA Span Tables for Joists and Rafters.

R502.2.3 1 Sleeping areas and attic joists. [IRC R502.3.1] Table R502.2.3 (1) shall be used to determine the maximum allowable span of floor joists that support sleeping areas and attics that are accessed by means of a fixed stairway in accordance with Section R311.5 provided that the design live load does not exceed 30 psf (1.44 kPa) and the design dead load does not exceed 20 psf (0.96 kPa). The allowable span of ceiling joists that support attics used for limited storage or no storage shall be determined in accordance with Section R802.2.2.

## TABLE R502.2.3(1) [IRC R502.3.1(1)]

## Floor Joist Spans for Common Lumber Species

## (Residential sleeping areas, live load=30psf, L/ =360)

| JOIST SPACING |  |  | DEAD LOAD = 10 psf |  |  |  | DEAD LOAD = 20 psf |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 2×6 | 2×8 | 2×10 | 2×12 | 2×6 | 2×8 | 2×10 | 2×12 |
|  |  |  | Maximum floor joist spans |  |  |  |  |  |  |  |
| (inches) | SPECIES AND GRADE |  | (ft - in.) | (ft - in.) | (ft - in.) | (ft - in.) | (ft - in.) | (ft - in.) | (ft - in.) | (ft - in.) |
|  | Douglas fir-larch Douglas fir-larch Douglas fir-larch Douglas fir-larch Hem-fir | SS #1 #2 #3 SS | 12- 6 12- 0 11-10 9- 8 11-10 | 16- 6 15-10 15- 7 12- 4 15- 7 | 21- 0 20- 3 19-10 15- 0 19-10 | 25- 7 24- 8 23- 0 17- 5 24- 2 | 12- 6 12- 0 11- 6 8- 8 11-10 | 16- 6 15- 7 14- 7 11- 0 15- 7 | 21- 0 19- 0 17- 9 13- 5 19-10 | 25- 7 22- 0 20- 7 15- 7 24- 2 |
|  | Hem-fir | #1 | 11- 7 | 15- 3 | 19- 5 | 23- 7 | 11- 7 | 15- 2 | 18- 6 | 21- 6 |
|  | Hem-fir | #2 | 11- 0 | 14- 6 | 18- 6 | 22- 6 | 11- 0 | 14- 4 | 17- 6 | 20- 4 |
| 12 | Hem-fir Southern pine Southern pine Southern pine Southern pine Spruce-pine-fir Spruce-pine-fir Spruce-pine-fir Spruce-pine-fir | #3 SS #1 #2 #3 SS #1 #2 #3 | 9- 8 12- 3 12- 0 11-10 10- 5 11- 7 11- 3 11- 3 9- 8 | 12- 4 16- 2 15-10 15- 7 13- 3 15- 3 14-11 14-11 12- 4 | 15- 0 20- 8 20- 3 19-10 15- 8 19- 5 19- 0 19- 0 15- 0 | 17- 5 25- 1 24- 8 24- 2 18- 8 23- 7 23- 0 23- 0 17- 5 | 8- 8 12- 3 12- 0 11-10 9- 4 11- 7 11- 3 11- 3 8- 8 | 11- 0 16- 2 15-10 15- 7 11-11 15- 3 14- 7 14- 7 11- 0 | 13- 5 20- 8 20- 3 18- 7 14- 0 19- 5 17- 9 17- 9 13- 5 | 15- 7 25- 1 24- 8 21- 9 16- 8 23- 7 20- 7 20- 7 15- 7 |
|  | Douglas fir-larch Douglas fir-larch Douglas fir-larch Douglas fir-larch Hem-fir | SS #1 #2 #3 SS | 11- 4 10-11 10- 9 8- 5 10- 9 | 15- 0 14- 5 14- 1 10- 8 14- 2 | 19- 1 18- 5 17- 2 13- 0 18- 0 | 23- 3 21- 4 19-11 15- 1 21-11 | 11- 4 10- 8 9-11 7- 6 10- 9 | 15- 0 13- 6 12- 7 9- 6 14- 2 | 19- 1 16- 5 15- 5 11- 8 18- 0 | 23- 0 19- 1 17-10 13- 6 21-11 |
|  | Hem-fir | #1 | 10- 6 | 13-10 | 17- 8 | 20- 9 | 10- 4 | 13- 1 | 16- 0 | 18- 7 |
|  | Hem-fir | #2 | 10- 0 | 13- 2 | 16-10 | 19- 8 | 9-10 | 12- 5 | 15- 2 | 17- 7 |
| 16 | Hem-fir Southern pine Southern pine Southern pine Southern pine Spruce-pine-fir Spruce-pine-fir Spruce-pine-fir Spruce-pine-fir | #3 SS #1 #2 #3 SS #1 #2 #3 | 8- 5 11- 2 10-11 10- 9 9- 0 10- 6 10- 3 10- 3 8- 5 | 10- 8 14- 8 14- 5 14- 2 11- 6 13-10 13- 6 13- 6 10- 8 | 13- 0 18- 9 18- 5 18- 0 13- 7 17- 8 17- 2 17- 2 13- 0 | 15- 1 22-10 22- 5 21- 1 16- 2 21- 6 19-11 19-11 15- 1 | 7- 6 11- 2 10-11 10- 5 8- 1 10- 6 9-11 9-11 7- 6 | 9- 6 14- 8 14- 5 13- 6 10- 3 13-10 12- 7 12- 7 9- 6 | 11- 8 18- 9 17-11 16- 1 12- 2 17- 8 15- 5 15- 5 11- 8 | 13- 6 22-10 21- 4 18-10 14- 6 21- 4 17-10 17-10 13- 6 |
|  | Douglas fir-larch Douglas fir-larch Douglas fir-larch Douglas fir-larch Hem-fir | SS #1 #2 #3 SS | 10- 8 10- 4 10-1 7- 8 10- 1 | 14- 1 13- 7 12-10 9- 9 13- 4 | 18- 0 16- 9 15- 8 11-10 17- 0 | 21-10 19- 6 18- 3 13- 9 20- 8 | 10- 8 9- 8 9- 1 6-10 10- 1 | 14- 1 12- 4 11- 6 8- 8 13- 4 | 18- 0 15- 0 14- 1 10- 7 17- 0 | 21- 0 17- 5 16- 3 12- 4 20- 7 |
|  | Hem-fir | #1 | 9-10 | 13- 0 | 16- 4 | 19- 0 | 9- 6 | 12- 0 | 14- 8 | 17- 0 |
|  | Hem-fir | #2 | 9- 5 | 12- 5 | 15- 6 | 17-1 | 8-11 | 11- 4 | 13-10 | 16- 1 |
| 19.2 | Hem-fir Southern pine Southern pine Southern pine Southern pine Spruce-pine-fir Spruce-pine-fir Spruce-pine-fir Spruce-pine-fir | #3 SS #1 #2 #3 SS #1 #2 #3 | 7- 8 10- 6 10- 4 10- 1 8- 3 9- 10 9- 8 9- 8 7- 8 | 9- 9 13-10 13- 7 13- 4 10- 6 13- 0 12- 9 12- 9 9- 9 | 11- 10 17- 8 17- 4 16- 5 12- 5 16- 7 15- 8 15- 8 11-10 | 13- 9 21- 6 21- 1 19- 3 14- 9 20- 2 18- 3 18- 3 13- 9 | 6-10 10- 6 10- 4 9- 6 7- 4 9-10 9- 1 9- 1 6-10 | 8- 8 13-10 13- 7 12- 4 9- 5 13- 0 11- 6 11- 6 8- 8 | 10- 7 17- 8 16- 4 14- 8 11- 1 16- 7 14- 1 14- 1 10- 7 | 12- 4 21- 6 19- 6 17- 2 13- 2 19- 6 16- 3 16- 3 12- 4 |
|  | Douglas fir-larch Douglas fir-larch Douglas fir-larch Douglas fir-larch Hem-fir | SS #1 #2 #3 SS | 9-11 9- 7 9- 1 6-10 9- 4 | 13- 1 12- 4 11- 6 8- 8 12- 4 | 16- 8 15- 0 14- 1 10- 7 15- 9 | 20- 3 17- 5 16- 3 12- 4 19- 2 | 9-11 8- 8 8- 1 6- 2 9- 4 | 13- 1 11- 0 10- 3 7- 9 12- 4 | 16- 2 13- 5 12- 7 9- 6 15- 9 | 18- 9 15- 7 14- 7 11- 0 18- 5 |
|  | Hem-fir | #1 | 9- 2 | 12- 0 | 14- 8 | 17- 0 | 8- 6 | 10- 9 | 13- 1 | 15- 2 |
|  | Hem-fir | #2 | 8- 9 | 11- 4 | 13-10 | 16- 1 | 8- 0 | 10- 2 | 12- 5 | 14- 4 |
| 24 | Hem-fir Southern pine Southern pine Southern pine Southern pine Spruce-pine-fir Spruce-pine-fir Spruce-pine-fir Spruce-pine-fir | #3 SS #1 #2 #3 SS #1 #2 #3 | 6-10 9- 9 9- 7 9- 4 7- 4 9- 2 8-11 8-11 6-10 | 8- 8 12-10 12- 7 12- 4 9- 5 12- 1 11- 6 11- 6 8- 8 | 10- 7 16- 5 16- 1 14- 8 11- 1 15- 5 14- 1 14- 1 10- 7 | 12- 4 19-11 19- 6 17- 2 13- 2 18- 9 16- 3 16- 3 12- 4 | 6- 2 9- 9 9- 7 8- 6 6- 7 9- 2 8- 1 8- 1 6- 2 | 7- 9 12-10 12- 4 11- 0 8- 5 12- 1 10- 3 10- 3 7- 9 | 9- 6 16- 5 14- 7 13- 1 9-11 15- 0 12- 7 12- 7 9- 6 | 11- 0 19-11 17- 5 15- 5 11-10 17- 5 14- 7 14- 7 11- 0 |

For SI: 1 inch = 25.4 mm, 1 foot = 304.8 mm, 1 pound per square foot = 0.0479 kPa.

NOTE: Check sources for availability of lumber in lengths greater than 20 feet.

a. Reserved. Dead load limits for townhouses in Seismic Design Category C and all structures in Seismic Design Categories D0, D1 and D2 shall be determined in accordance with Section R301.2.2.2.1.

TABLE R502.2.3(2) [IRC R502.3.1(2)]

Floor Joist Spans for Common Lumber Species

(Residential sleeping areas, live load=40psf, L/ =360)

| JOIST SPACING (inches) | SPECIES AND GRADE |  | DEAD LOAD = 10 psf |  |  |  | DEAD LOAD = 20 psf |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 2×6 | 2×8 | 2×10 | 2×12 | 2×6 | 2×8 | 2×10 | 2×12 |
|  |  |  | Maximum floor joist spans |  |  |  |  |  |  |  |
|  |  |  | (ft - in.) | (ft - in.) | (ft - in.) | (ft - in.) | (ft - in.) | (ft - in.) | (ft - in.) | (ft - in.) |
| 12 | Douglas fir-larch Douglas fir-larch Douglas fir-larch Douglas fir-larch Hem-fir Hem-fir Hem-fir Hem-fir Southern pine Southern pine Southern pine Southern pine Spruce-pine-fir Spruce-pine-fir Spruce-pine-fir Spruce-pine-fir | SS #1 #2 #3 SS #1 #2 #3 SS #1 #2 #3 SS #1 #2 #3 | 11- 4 10-11 10- 9 8- 8 10- 9 10- 6 10- 0 8- 8 11- 2 10-11 10- 9 9- 4 10- 6 10- 3 10- 3 8- 8 | 15- 0 14- 5 14- 2 11- 0 14- 2 13-10 13- 2 11- 0 14- 8 14- 5 14- 2 11-11 13-10 13- 6 13- 6 11- 0 | 19- 1 18- 5 17- 9 13- 5 18- 0 17- 8 16-10 13- 5 18- 9 18- 5 18- 0 14- 0 17- 8 17- 3 17- 3 13- 5 | 23- 3 22- 0 20- 7 15- 7 21-11 21- 6 20- 4 15- 7 22-10 22- 5 21- 9 16- 8 21- 6 20- 7 20- 7 15- 7 | 11- 4 10-11 10- 6 7-11 10- 9 10- 6 10- 0 7-11 11- 2 10-11 10- 9 8- 6 10- 6 10- 3 10- 3 7-11 | 15- 0 14- 2 13- 3 10- 0 14- 2 13-10 13- 1 10- 0 14- 8 14- 5 14- 2 10-10 13-10 13- 3 13- 3 10- 0 | 19- 1 17- 4 16- 3 12- 3 18- 0 16-11 16- 0 12- 3 18- 9 18- 5 16-11 12-10 17- 8 16- 3 16- 3 12- 3 | 23- 3 20- 1 18-10 14- 3 21-11 19- 7 18- 6 14- 3 22-10 22- 5 19-10 15- 3 21- 6 18-10 18-10 14- 3 |
| 16 | Douglas fir-larch Douglas fir-larch Douglas fir-larch Douglas fir-larch Hem-fir Hem-fir Hem-fir Hem-fir Southern pine Southern pine Southern pine Southern pine Spruce-pine-fir Spruce-pine-fir Spruce-pine-fir Spruce-pine-fir | SS #1 #2 #3 SS #1 #2 #3 SS #1 #2 #3 SS #1 #2 #3 | 10- 4 9-11 9- 9 7- 6 9- 9 9- 6 9- 1 7- 6 10- 2 9-11 9- 9 8- 1 9- 6 9- 4 9- 4 7- 6 | 13- 7 13- 1 12- 7 9- 6 12-10 12- 7 12- 0 9- 6 13- 4 13- 1 12-10 10- 3 12- 7 12- 3 12- 3 9- 6 | 17- 4 16- 5 15- 5 11- 8 16- 5 16- 0 15- 2 11- 8 17- 0 16- 9 16- 1 12- 2 16- 0 15- 5 15- 5 11- 8 | 21- 1 19- 1 17-10 13- 6 19-11 18- 7 17- 7 13- 6 20- 9 20- 4 18-10 14- 6 19- 6 17-10 17-10 13- 6 | 10- 4 9- 8 9- 1 6-10 9- 9 9- 6 8-11 6-10 10- 2 9-11 9- 6 7- 4 9- 6 9- 1 9- 1 6-10 | 13- 7 12- 4 11- 6 8- 8 12-10 12- 0 11- 4 8- 8 13- 4 13- 1 12- 4 9- 5 12- 7 11- 6 11- 6 8- 8 | 17- 4 15- 0 14- 1 10- 7 16- 5 14- 8 13-10 10- 7 17- 0 16- 4 14- 8 11- 1 16- 0 14- 1 14- 1 10- 7 | 21- 0 17- 5 16- 3 12- 4 19-11 17- 0 16- 1 12- 4 20- 9 19- 6 17- 2 13- 2 19- 6 16- 3 16- 3 12- 4 |
| 19.2 | Douglas fir-larch Douglas fir-larch Douglas fir-larch Douglas fir-larch Hem-fir Hem-fir Hem-fir Hem-fir Southern pine Southern pine Southern pine Southern pine Spruce-pine-fir Spruce-pine-fir Spruce-pine-fir Spruce-pine-fir | SS #1 #2 #3 SS #1 #2 #3 SS #1 #2 #3 SS # #2 #3 | 9- 8 9- 4 9- 1 6-10 9- 2 9- 0 8- 7 6-10 9- 6 9- 4 9- 2 7- 4 9- 0 8- 9 8- 9 6-10 | 12-10 12- 4 11- 6 8- 8 12- 1 11-10 11- 3 8- 8 12- 7 12- 4 12- 1 9- 5 11-10 11- 6 11- 6 8- 8 | 16- 4 15- 0 14- 1 10- 7 15- 5 14- 8 13-10 10- 7 16- 0 15- 9 14- 8 11- 1 15- 1 14- 1 14- 1 10- 7 | 19-10 17- 5 16- 3 12- 4 18- 9 17- 0 16- 1 12- 4 19- 6 19- 2 17- 2 13- 2 18- 4 16- 3 16- 3 12- 4 | 9- 8 8-10 8- 3 6- 3 9- 2 8- 8 8- 2 6- 3 9- 6 9- 4 8- 8 6- 9 9- 0 8- 3 8- 3 6- 3 | 12-10 11- 3 10- 6 7-11 12- 1 10-11 10- 4 7-11 12- 7 12- 4 11- 3 8- 7 11-10 10- 6 10- 6 7-11 | 16- 4 13- 8 12-10 9- 8 15- 5 13- 4 12- 8 9- 8 16- 0 14-11 13- 5 10- 1 15- 1 12-10 12-10 9- 8 | 19- 2 15-11 14-10 11- 3 18- 9 15- 6 14- 8 11- 3 19- 6 17- 9 15- 8 12- 1 17- 9 14-10 14-10 11- 3 |
| 24 | Douglas fir-larch Douglas fir-larch Douglas fir-larch Douglas fir-larch Hem-fir Hem-fir Hem-fir Hem-fir Southern pine Southern pine Southern pine Southern pine Spruce-pine-fir Spruce-pine-fir Spruce-pine-fir Spruce-pine-fir | SS #1 #2 #3 SS #1 #2 #3 SS #1 #2 #3 SS #1 #2 #3 | 9- 0 8- 8 8- 1 6- 2 8- 6 8- 4 7-11 6- 2 8-10 8- 8 8- 6 6- 7 8- 4 8- 1 8- 1 6- 2 | 11-11 11- 0 10- 3 7- 9 11- 3 10- 9 10- 2 7- 9 11- 8 11- 5 11- 0 8- 5 11- 0 10- 3 10- 3 7- 9 | 15- 2 13- 5 12- 7 9- 6 14- 4 13- 1 12- 5 9- 6 14-11 14- 7 13- 1 9-11 14- 0 12- 7 12- 7 9- 6 | 18- 5 15- 7 14- 7 11- 0 17- 5 15- 2 14- 4 11- 0 18- 1 17- 5 15- 5 11-10 17- 0 14- 7 14- 7 11- 0 | 9- 0 7-11 7- 5 5- 7 8- 6 7- 9 7- 4 5- 7 8-10 8- 8 7- 9 6- 0 8- 4 7- 5 7- 5 5- 7 | 11-11 10- 0 9- 5 7- 1 11- 3 9- 9 9- 3 7- 1 11- 8 11- 3 10- 0 7- 8 11- 0 9- 5 9- 5 7- 1 | 14- 9 12- 3 11- 6 8- 8 14- 4 11-11 11- 4 8- 8 14-11 13- 4 12- 0 9- 1 13- 8 11- 6 11- 6 8- 8 | 17- 1 14- 3 13- 4 10- 1 16-10a 13-10 13- 1 10- 1 18- 1 15-11 14- 0 10- 9 15-11 13- 4 13- 4 10- 1 |

For SI: 1 inch = 25.4 mm, 1 foot = 304.8 mm, 1 pound per square foot = 0.0479 kPa.

NOTE: Check sources for availability of lumber in lengths greater than 20 feet.

a. End bearing length shall be increased to 2 inches.

b. Reserved.  Dead load limits for townhouses in Seismic Design Category C and all structures in Seismic Design Categories D0, D1, and D2 shall be determined in accordance with Section R301.2.2.2.1.

R502.2.3.2 Other floor joists.  IRC R502.3.2]Table R502.2.3 (2) shall be used to determine the maximum allowable span of floor joists that support all other areas of the building, other than sleeping rooms and attics, provided that the design live load does not exceed 40 psf (1.92 kPa) and the design dead load does not exceed 20 psf (0.96 kPa). [

R502.2.3.3 Floor cantilevers. [IRC R502.3.3] Floor cantilever spans shall not exceed the nominal depth of the wood floor joist. Floor cantilevers constructed in accordance with Table R502.2.3.3.(1) shall be -*permitted when supporting a light-frame bearing wall and roof only. Floor cantilevers supporting an exterior balcony are permitted to be constructed in accordance with Table R502.2.3.3.(2).

TABLE R502.2.3.3(1) [IRC R502.3.3(1)]

CANTILEVER SPANS FOR FLOOR JOISTS SUPPORTING LIGHT-FRAME EXTERIOR BEARING WALL AND ROOF ONLY a, b, c, f, g, h

(Floor Live Load 40 psf, Roof Live Load 20 psf)

| Member & Spacing | Maximum Cantilever Span (Uplift Force at Backspan Support in Lbs.)d, e |  |  |
| --- | --- | --- | --- |
|  | Roof Width |  |  |
|  | 24 ft | 32 ft | 40 ft |
| 2 × 8 @ 12″ | 20″ (177) | 15″ (227) | - |
| 2 × 10 @ 16″ | 29″ (228) | 21″ (297) | 16″ (364) |
| 2 × 10 @ 12″ | 36″ (166) | 26″ (219) | 20″ (270) |
| 2 × 12 @ 16″ | - | 32″ (287) | 25″ (356) |
| 2 × 12 @ 12″ | - | 42″ (209) | 31″ (263) |
| 2 × 12 @ 8″ | - | 48″ (136) | 45″ (169) |

For SI: 1 inch = 25.4 mm, 1 pound per square foot = 0.0479kPa.

a. Tabulated values are for clear-span roof supported solely by exterior bearing walls.

b. Spans are based on No. 2 Grade lumber of Douglas fir-larch, hem-fir, southern pine, and spruce-pine-fir for repetitive (3 or more) members.

c. Ratio of backspan to cantilever span shall be at least 3:1.

d. Connections capable of resisting the indicated uplift force shall be provided at the backspan support.

e. Uplift force is for a backspan to cantilever span ratio of 3:1. Tabulated uplift values are permitted to be reduced by multiplying by a factor equal to 3 divided by the actual backspan ratio provided (3/backspan ratio).

f. Reserved.

g. A full-depth rim joist shall be provided at the unsupported end of  the cantilevered  joists. Solid blocking shall be provided at the  supported end.

h. Reserved.

TABLE R502.2.3.3(2) [IRC R502.3.3(2)]

CANTILEVER SPANS FOR FLOOR JOISTS

SUPPORTING EXTERIOR BALCONY a, b, e, f

| Member Size | Spacing | Maximum Cantilever Span (Uplift Force at Backspan Support in lb)c, d |
| --- | --- | --- |
| 2 × 8 | 12″ | 42″ (139) |
| 2 × 8 | 16″ | 36″ (151) |
| 2 × 10 | 12″ | 61″ (164) |
| 2 × 10 | 16″ | 53″ (180) |
| 2 × 10 | 24″ | 43″ (212) |
| 2 × 12 | 16″ | 72″ (228) |
| 2 × 12 | 24″ | 58″ (279) |

For SI: 1 inch = 25.4 mm, 1 pound per square foot = 0.0479kPa.

a. Spans are based on No. 2 Grade lumber of Douglas fir-larch, hem-fir, southern pine, and spruce-pine-fir for repetitive (3 or more) members.

b. Ratio of backspan to cantilever span shall be at least 2:1.

c. Connections capable of resisting the indicated uplift force shall be provided at the backspan support.

d. Uplift force is for a backspan to cantilever span ratio of 2:1. Tabulated uplift values are permitted to be reduced by multiplying by a factor  equal to 2 divided by the actual backspan ratio provided (2/backspan ratio).

e. A full-depth rim joist shall be provided at the supported end of  the cantilevered  joists. Solid blocking shall be provided at the  supported end.

f. Reserved.

R502.2.4 Joists under bearing partitions [IRC R502.4].  Joists under parallel bearing partitions shall be of adequate size to support the load. Double joists, sized to adequately support the load, that are separated to permit the installation of piping or vents shall be full depth solid blocked with lumber not less than 2 inches (51 mm) in nominal thickness spaced not more than 4 feet (1219 mm) on center. Bearing partitions perpendicular to joists shall not be offset from supporting girders, walls or partitions more than the joist depth unless such joists are of sufficient size to carry the additional load.

R502.2.5 Allowable girder spans [IRC R502.5]. The allowable spans of girders fabricated of dimension lumber shall not exceed the values set forth in Tables R502.2.5 (1) and R502.2.5 (2).

TABLE R502.2.5(1) [IRC R502.5(1)] GIRDER SPANS AND HEADER SPANS FOR EXTERIOR BEARING WALLS

(Maximum spans for Douglas fir-larch, hem-fir, southern pine and spruce-pine-firb and required number of jack studs)

| GIRDERS AND HEADERS SUPPORTING | SIZE | Building Widthc(feet) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 20 |  | 28 |  | 36 |  |
|  |  | Span | NJd | Span | NJd | Span | NJd |
| Roof and ceiling | 2-2 × 4 | 3-6 | 1 | 3-2 | 1 | 2-10 | 1 |
|  | 2-2 × 6 | 5-5 | 1 | 4-8 | 1 | 4-2 | 1 |
|  | 2-2 × 8 | 6-10 | 1 | 5-11 | 2 | 5-4 | 2 |
|  | 2-2 × 10 | 8-5 | 2 | 7-3 | 2 | 6-6 | 2 |
|  | 2-2 × 12 | 9-9 | 2 | 8-5 | 2 | 7-6 | 2 |
|  | 3-2 × 8 | 8-4 | 1 | 7-5 | 1 | 6-8 | 1 |
|  | 3-2 × 10 | 10-6 | 1 | 9-1 | 2 | 8-2 | 2 |
|  | 3-2 × 12 | 12-2 | 2 | 10-7 | 2 | 9-5 | 2 |
|  | 4-2 × 8 | 9-2 | 1 | 8-4 | 1 | 7-8 | 1 |
|  | 4-2 × 10 | 11-8 | 1 | 10-6 | 1 | 9-5 | 2 |
|  | 4-2 × 12 | 14-1 | 1 | 12-2 | 2 | 10-11 | 2 |
| Roof, ceiling and one center-bearing floor | 2-2 × 4 | 3-1 | 1 | 2-9 | 1 | 2-5 | 1 |
|  | 2-2 × 6 | 4-6 | 1 | 4-0 | 1 | 3-7 | 2 |
|  | 2-2 × 8 | 5-9 | 2 | 5-0 | 2 | 4-6 | 2 |
|  | 2-2 × 10 | 7-0 | 2 | 6-2 | 2 | 5-6 | 2 |
|  | 2-2 × 12 | 8-1 | 2 | 7-1 | 2 | 6-5 | 2 |
|  | 3-2 × 8 | 7-2 | 1 | 6-3 | 2 | 5-8 | 2 |
|  | 3-2 × 10 | 8-9 | 2 | 7-8 | 2 | 6-11 | 2 |
|  | 3-2 × 12 | 10-2 | 2 | 8-11 | 2 | 8-0 | 2 |
|  | 4-2 × 8 | 8-1 | 1 | 7-3 | 1 | 6-7 | 1 |
|  | 4-2 × 10 | 10-1 | 1 | 8-10 | 2 | 8-0 | 2 |
|  | 4-2 × 12 | 11-9 | 2 | 10-3 | 2 | 9-3 | 2 |
| Roof, ceiling and one clear span floor | 2-2 × 4 | 2-8 | 1 | 2-4 | 1 | 2-1 | 1 |
|  | 2-2 × 6 | 3-11 | 1 | 3-5 | 2 | 3-0 | 2 |
|  | 2-2 × 8 | 5-0 | 2 | 4-4 | 2 | 3-10 | 2 |
|  | 2-2 × 10 | 6-1 | 2 | 5-3 | 2 | 4-8 | 2 |
|  | 2-2 × 12 | 7-1 | 2 | 6-1 | 3 | 5-5 | 3 |
|  | 3-2 × 8 | 6-3 | 2 | 5-5 | 2 | 4-10 | 2 |
|  | 3-2 × 10 | 7-7 | 2 | 6-7 | 2 | 5-11 | 2 |
|  | 3-2 × 12 | 8-10 | 2 | 7-8 | 2 | 6-10 | 2 |
|  | 4-2 × 8 | 7-2 | 1 | 6-3 | 2 | 5-7 | 2 |
|  | 4-2 × 10 | 8-9 | 2 | 7-7 | 2 | 6-10 | 2 |
|  | 4-2 × 12 | 10-2 | 2 | 8-10 | 2 | 7-11 | 2 |
| Roof, ceiling and two center-bearing floors | 2-2 × 4 | 2-7 | 1 | 2-3 | 1 | 2-0 | 1 |
|  | 2-2 × 6 | 3-9 | 2 | 3-3 | 2 | 2-11 | 2 |
|  | 2-2 × 8 | 4-9 | 2 | 4-2 | 2 | 3-9 | 2 |
|  | 2-2 × 10 | 5-9 | 2 | 5-1 | 2 | 4-7 | 3 |
|  | 2-2 × 12 | 6-8 | 2 | 5-10 | 3 | 5-3 | 3 |
|  | 3-2 × 8 | 5-11 | 2 | 5-2 | 2 | 4-8 | 2 |
|  | 3-2 × 10 | 7-3 | 2 | 6-4 | 2 | 5-8 | 2 |
|  | 3-2 × 12 | 8-5 | 2 | 7-4 | 2 | 6-7 | 2 |
|  | 4-2 × 8 | 6-10 | 1 | 6-0 | 2 | 5-5 | 2 |
|  | 4-2 × 10 | 8-4 | 2 | 7-4 | 2 | 6-7 | 2 |
|  | 4-2 × 12 | 9-8 | 2 | 8-6 | 2 | 7-8 | 2 |

(continued)

TABLE R502.2.5(1)-continued GIRDER SPANSa AND HEADER SPANSa FOR EXTERIOR BEARING WALLS (Maximum spans for Douglas fir-larch, hem-fir, southern pine and spruce-pine-firb and required number of jack studs)

| GIRDERS AND HEADERS SUPPORTING | SIZE | Building Widthc(feet) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 20 |  | 28 |  | 36 |  |
|  |  | Span | NJd | Span | NJd | Span | NJd |
| Roof, ceiling and two clear span floor | 2-2 × 4 | 2-1 | 1 | 1-8 | 1 | 1-6 | 2 |
|  | 2-2 × 6 | 3-1 | 2 | 2-8 | 2 | 2-4 | 2 |
|  | 2-2 × 8 | 3-10 | 2 | 3-4 | 2 | 3-0 | 3 |
|  | 2-2 × 10 | 4-9 | 2 | 4-1 | 3 | 3-8 | 3 |
|  | 2-2 × 12 | 5-6 | 3 | 4-9 | 3 | 4-3 | 3 |
|  | 3-2 × 8 | 4-10 | 2 | 4-2 | 2 | 3-9 | 2 |
|  | 3-2 × 10 | 5-11 | 2 | 5-1 | 2 | 4-7 | 3 |
|  | 3-2 × 12 | 6-10 | 2 | 5-11 | 3 | 5-4 | 3 |
|  | 4-2 × 8 | 5-7 | 2 | 4-10 | 2 | 4-4 | 2 |
|  | 4-2 × 10 | 6-10 | 2 | 5-11 | 2 | 5-3 | 2 |
|  | 4-2 × 12 | 7-11 | 2 | 6-10 | 2 | 6-2 | 3 |

For SI: 1 inch = 25.4 mm, 1 pound per square foot = 0.0479kPa.

a. Spans are given in feet and inches.

b. Tabulated values assume #2 grade lumber.

c. Building width is measured perpendicular to the ridge. For widths between those shown, spans are permitted to be interpolated.

d. NJ - Number of jack studs required to support each end. Where the number of required jack studs equals one, the header is permitted to be supported by an approved framing anchor attached to the full-height wall stud and to the header.

e.  Reserved.

TABLE R502.2.5(2) [IRC R502.5(2)]
GIRDER SPANS AND HEADER SPANS FOR INTERIOR BEARING WALLS

(Maximum spans for Douglas fir-larch, hem-fir, southern pine and spruce-pine-firb and required number of jack studs)

| HEADERS AND GIRDERS SUPPORTING | SIZE | BUILDING WIDTHc (feet) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 20 |  | 28 |  | 36 |  |
|  |  | Span | NJd | Span | NJd | Span | NJd |
| One floor only | 2-2×4 | 3-1 | 1 | 2-8 | 1 | 2-5 | 1 |
|  | 2-2×6 | 4-6 | 1 | 3-11 | 1 | 3-6 | 1 |
|  | 2-2×8 | 5-9 | 1 | 5-0 | 2 | 4-5 | 2 |
|  | 2-2×10 | 7-0 | 2 | 6-1 | 2 | 5-5 | 2 |
|  | 2-2×12 | 8-1 | 2 | 7-0 | 2 | 6-3 | 2 |
|  | 3-2×8 | 7-2 | 1 | 6-3 | 1 | 5-7 | 2 |
|  | 3-2×10 | 8-9 | 1 | 7-7 | 2 | 6-9 | 2 |
|  | 3-2×12 | 10-2 | 2 | 8-10 | 2 | 7-10 | 2 |
|  | 4-2×8 | 9-0 | 1 | 7-8 | 1 | 6-9 | 1 |
|  | 4-2×10 | 10-1 | 1 | 8-9 | 1 | 7-10 | 2 |
|  | 4-2×12 | 11-9 | 1 | 10-2 | 2 | 9-1 | 2 |
| Two floors | 2-2×4 | 2-2 | 1 | 1-10 | 1 | 1-7 | 1 |
|  | 2-2×6 | 3-2 | 2 | 2-9 | 2 | 2-5 | 2 |
|  | 2-2×8 | 4-1 | 2 | 3-6 | 2 | 3-2 | 2 |
|  | 2-2×10 | 4-11 | 2 | 4-3 | 2 | 3-10 | 3 |
|  | 2-2×12 | 5-9 | 2 | 5-0 | 3 | 4-5 | 3 |
|  | 3-2×8 | 5-1 | 2 | 4-5 | 2 | 3-11 | 2 |
|  | 3-2×10 | 6-2 | 2 | 5-4 | 2 | 4-10 | 2 |
|  | 3-2×12 | 7-2 | 2 | 6-3 | 2 | 5-7 | 3 |
|  | 4-2×8 | 6-1 | 1 | 5-3 | 2 | 4-8 | 2 |
|  | 4-2×10 | 7-2 | 2 | 6-2 | 2 | 5-6 | 2 |
|  | 4-2×12 | 8-4 | 2 | 7-2 | 2 | 6-5 | 2 |

For SI: 1 inch = 25.4 mm, 1 foot = 304.8 mm.

a. Spans are given in feet and inches.

b. Tabulated values assume #2 grade lumber.

c. Building width is measured perpendicular to the ridge. For widths between those shown, spans are permitted to be interpolated.

d. NJ - Number of jack studs required to support each end. Where the number of required jack studs equals one, the header is permitted to be supported by an approved framing anchor attached to the full-height wall stud and to the header.

R502.2.6 Bearing [IRC R502.6].  The ends of each joist, beam or girder shall have not less than 1.5 inches (38 mm) of bearing on wood or metal and not less than 3 inches (76 mm) on masonry or concrete except where supported on a 1-inch-by-4-inch (25.4 mm by 102 mm) ribbon strip and nailed to the adjacent stud or by the use of approved joist hangers.

R502.2.6.1 Floor systems [IRC R502.6.1].  Joists framing from opposite sides over a bearing support shall lap a minimum of 3 inches (76 mm) and shall be nailed together with a minimum three 10d face nails. A wood or metal splice with strength equal to or greater than that provided by the nailed lap is permitted.

R502.2.6.2 Joist framing [IRC R502.6.2]. Joists framing into the side of a wood girder shall be supported by approved framing anchors or on ledger strips not less than nominal 2 inches by 2 inches (51 mm by 51 mm).

R502.2.7 Lateral restraint at supports [IRC R502.7]. Joists shall be supported laterally at the ends by full-depth solid blocking not less than 2 inches (51 mm) nominal in thickness; or by attachment to a full-depth header, band, or rim joist, or to an adjoining stud; or shall be otherwise provided with lateral support to prevent rotation.

Exceptions:

1. Trusses, structural composite lumber, structural glued-laminated members and I-joists shall be supported laterally as required by the manufacturer’s recommendations.

2. Reserved. In Seismic Design Categories D0, D1 and D2, lateral restraint shall also be provided at each intermediate support.

R502.2.7.1 Bridging [IRC R502.7.1].  Joists exceeding a nominal 2 inches by 12 inches (51 mm by 305 mm) shall be supported laterally by solid blocking, diagonal bridging (wood or metal), or a continuous 1-inch-by-3-inch (25.4 mm by 76 mm) strip nailed across the bottom of joists perpendicular to joists at intervals not exceeding 8 feet (2438 mm).

Exception:

1. Trusses, structural composite lumber, structural glued-laminated members and I-joists shall be supported laterally as required by the manufacturer’s recommendations.

R502.2.8 Drilling and notching [IRC R502.8]. Structural floor members shall not be cut, bored or notched in excess of the limitations specified in this section. See Figure R502.2.8.

R502.2.8.1 Sawn lumber [IRC R502.8.1].  Notches in solid lumber joists, rafters and beams shall not exceed one-sixth of the depth of the member, shall not be longer than one-third of the depth of the member and shall not be located in the middle one-third of the span. Notches at the ends of the member shall not exceed one-fourth the depth of the member. The tension side of members 4 inches (102 mm) or greater in nominal thickness shall not be notched except at the ends of the members. The diameter of holes bored or cut into members shall not exceed one-third the depth of the member. Holes shall not be closer than 2 inches (51 mm) to the top or bottom of the member, or to any other hole located in the member. Where the member is also notched, the hole shall not be closer than 2 inches (51 mm) to the notch.

R502.2.8 2 Engineered wood products [IRC R502.8.2]. Cuts, notches and holes bored in trusses, structural composite lumber, structural glue-laminated members or I-joists are prohibited except where permitted by the manufacturer’s recommendations or where the effects of such alterations are specifically considered in the design of the member by a registered design professional.

FIGURE R 502.2.8 [IRC R502.8]
CUTTING, NOTCHING AND DRILLING

R502.2.9 Fastening [IRC R502.9]. Floor framing shall be nailed in accordance with Table R602.2(1) Where posts and beam or girder construction is used to support floor framing, positive connections shall be provided to ensure against uplift and lateral displacement.

R502.2.10 Framing of openings [IRC R502.10].  Openings in floor framing shall be framed with a header and trimmer joists. When the header joist span does not exceed 4 feet (1219 mm), the header joist may be a single member the same size as the floor joist. Single trimmer joists may be used to carry a single header joist that is located within 3 feet (914 mm) of the trimmer joist bearing.

When the header joist span exceeds 4 feet (1219 mm), the trimmer joists and the header joist shall be doubled and of sufficient cross section to support the floor joists framing into the header. Approved hangers shall be used for the header joist to trimmer joist connections when the header joist span exceeds 6 feet (1829 mm). Tail joists over 12 feet (3658 mm) long shall be supported at the header by framing anchors or on ledger strips not less than 2 inches by 2 inches (51 mm by 51 mm).

R502.3 Add to read as shown:

R502.3 Design and construction where wind speed is 100 mph or greater. Floor framing of light-frame wood construction shall be designed and constructed in accordance with the provisions of Section R301.2.1.1, Section R502.1.

R503.2.3 Installation. Wood structural panels used as subfloor or combination subfloor underlayment shall be attached to wood framing in accordance with Table R602.2(1) and shall be attached to cold-formed steel framing in accordance with Table R505.3.1(2).

R503.3.3 Installation. Particleboard underlayment shall be installed in accordance with the recommendations of the manufacturer and attached to framing in accordance with Table R602.2(1).

Table R505.3.1(1) Change to read as follows [use table as per the 2007 FBC-R]:

Table R505.3.1(1)

FLOOR TO FOUNDATION OR BEARING WALL CONNECTION REQUIREMENTS a,b

| FRAMING CONDITION | WIND SPEED (mph) AND EXPOSURE |  |
| --- | --- | --- |
|  | Less than 100 A/B | Less than 100 C |
| Floor joist to wall track of exterior steel load-bearing wall per Figure R505.3.1(1) | 2-No. 8 screws | 3-No. 8 screws |
| Floor joist track to wood sill per Figure R505.3.1(2) | Steel plate spaced at 3′ o.c., with 4-No. 8 screws and 4-10d or 6-8d common nails | Steel plate, spaced at 2′ o.c., with 4-No. 8 screws and 4-10d or 6-8d common nails |
| Floor joist track to foundation per Figure R505.3.1(3) | 1/2″ minimum diameter anchor bolt and clip angle spaced at 6′ o.c. with 8-No. 8 screws | 1/2″ minimum diameter anchor bolt and clip angle spaced at 4′ o.c. with 8-No. 8 screws |
| Joist cantilever to wall track per Figure R505.3.1(4) | 2-No. 8 screws per stiffener or bent plate | 3-No. 8 screws per stiffener or bent plate |
| Joist cantilever to wood sill per Figure R505.3.1(5) | Steel plate spaced at 3′ o.c., with 4-No. 8 screws and 4-10d or 6-8d common nails | Steel plate spaced at 2′ o.c., with 4-No. 8 screws and 4-10d or 6-8d common nails |
| Joist cantilever to foundation per Figure R505.3.1(6) | 1/2″ minimum diameter anchor bolt and clip angle spaced at 6′ o.c. with 8-No. 8 screws | 1/2″ minimum diameter anchor bolt and clip angle spaced at 4′ o.c. with 8-No. 8 screws |

[Add footnotes, etc.]

TABLE R505.3.4(1)

CLIP ANGLE BEARING STIFFENERS

(20 psf equivalent snow load)  Reserved.

TABLE R505.3.4(2)

CLIP ANGLE BEARING STIFFENERS

(30 psf equivalent snow load)  Reserved.

TABLE R505.3.4(3)

CLIP ANGLE BEARING STIFFENERS

(50 psf equivalent snow load)  Reserved.

TABLE R505.3.4(4)

CLIP ANGLE BEARING STIFFENERS

(70 psf equivalent snow load)  Reserved.

- R506.2.5 Add to read as shown:

- R506.2.5 Joints.  Concrete slabs on ground shall be provided with joints in accordance with ACI 224.3R or other approved methods. Joints shall be designed by an architect or engineer.           Exception: Joints are not required in unreinforced plain concrete slabs on ground or in slabs for one- and two-family dwellings complying with one of the following:

- 1.	Concrete slabs on ground containing synthetic fiber reinforcement. Fiber lengths and dosage amounts shall comply with one of the following

- (1)	Fiber lengths shall be ½ inch to 2 inches (13 to 51 mm) in length. Dosage amounts shall be from 0.75 to 1.5 pounds per cubic yard (0.45 to 0.89 kg/m3) in accordance with the manufacturer’s recommendations. Synthetic fibers shall comply with ASTM C 1116. The manufacturer or supplier shall provide certification of compliance with ASTM C 1116 when requested by the building official; or,

- (2)	Fiber length shall be from ½ inch to 2 inches (13 mm to 51 mm) in length, monofilament or fibrillated. Dosage amounts shall be from 0.5 to 1.5 pounds per cubic yard (0.30 to 0.89 kg/m3) to achieve minimum 40 percent reduction of plastic shrinkage cracking of concrete versus a control mix in accordance with ICBO AC32. Independent test results using minimum six (6) test specimens shall be provided to the building official showing compliance with ICBO A32. Synthetic fiber shall comply with ASTM C1116, Paragraph 4.1.3, Type III. The manufacturer or supplier shall provide certification of compliance with ASTM C1116 when requested by building official.

2.	Concrete slabs on ground containing 6x6 W1.4 × W1.4 welded wire reinforcement fabric located in the middle to the upper one-third of the slab. Welded wire reinforcement fabric shall be supported with approved materials or supports at spacings not to exceed 3 feet (914 mm) or in accordance with the manufacturer’s specifications. Welded plain wire reinforcement fabric for concrete shall conform to ASTM A 185, Standard Specification for Steel Welded Wire Reinforcement Fabric, Plain, for Concrete Reinforcement.

CHAPTER 6 WALL CONSTRUCTION

IRC ’09 added the following section to the code. It is not applicable in Florida (climate zones 2 and 1) and should be reserved.

R601.3 Vapor retarders. Reserved. Class I or II vapor retarders are required on the interior side of frame walls in Zones 5, 6, 7, 8 and Marine 4.

R601.3.1 Class III vapor retarders. Reserved.

R601.3.2 Material vapor retarder class.  Reserved.

R601.3.3 Minimum clear air spaces and vented openings for vented cladding. Reserved.

TABLE R601.3.1 CLASS III VAPOR RETARDERS. Reserved. [delete Table R601.3.1]

Revise Section R602.1. Renumber as follows:

R602.1 General requirements.

R602.1.1 Identification.  Load-bearing…accepted.

R602.1.1.1 End-jointed lumber…

R602.1.1.2 Structural glued laminated timbers….

R602.1.1.3 Structural log members. …

Change Section R602.1.2 to read as follows:

R602.1.2 Fireblocking required (IRC R602.8) Fireblocking shall be provided in accordance with Section R302.11.

R602.1.3 [IRC R602.7.2] Nonbearing walls. Load-bearing headers are not required in interior or exterior nonbearing walls. A single flat 2-inch-by-4-inch (51 mm by 102 mm) member may be

used as a header in interior or exterior nonbearing walls for openings up to 8 feet (2438 mm) in width if the vertical distance to the parallel nailing surface above is not more than 24 inches (610 mm). For such nonbearing headers, no cripples or blocking are required above the header.

R602.1.3.1 [IRC R602.5] Interior nonbearing walls. Interior nonbearing walls shall be permitted to be constructed with 2-inch-by-3-inch (51 mm by 76 mm) studs spaced 24 inches (610 mm) on center or, when not part of a braced wall line, 2-inch-by-4-inch (51 mm by 102 mm) flat studs spaced at 16 inches (406 mm) on center. Interior nonbearing walls shall be capped with at least a single top plate. Interior nonbearing walls shall be fireblocked in accordance with Section R302.11 R602.8.

Overlap with Florida Specific – Structural TAC

R602.3  Change to read as follows:

FBC

R602.2  Design and construction where wind speed is less than 100 miles per hour (45 m/s). Exterior walls of wood-frame construction shall be designed and constructed in accordance with the provisions of this Section and Figures R602.2(1) and R602.2(2) or in accordance with AF&PA’s NDS. Components of exterior walls shall be fastened in accordance with Tables R602.2(1) through R602.2(4). Exterior walls covered with foam plastic sheathing shall be braced in accordance with Section R602.2.10. Structural sheathing shall be fastened directly to structural framing members.

IRC ’09 R602.3 is changed to read as shown. Resolve potential conflicts.

R602.2 Design and construction. Exterior walls of wood-frame construction shall be designed and constructed in accordance with the provisions of this chapter and Figures

R602.3(1) and R602.3.(2) or in accordance with AF&PA’s NDS. Components of exterior walls shall be fastened in accordance with Tables R602.3(1) through R602.3(4). Structural sheathing shall be fastened directly to structural framing members. Exterior wall coverings shall be capable of resisting the wind pressures listed in Table R301.2(2) adjusted for height and exposure using Table R301.2(3). Wood structural panel sheathing used for exterior walls shall conform to the requirements of Table R602.3(3).

Studs shall be continuous from support at the sole plate to a support at the top plate to resist loads perpendicular to the wall. The support shall be a foundation or floor, ceiling or roof diaphragm or shall be designed in accordance with accepted engineering practice.

Exception: Jack studs, trimmer studs and cripple studs at openings in walls that comply with Tables R502.5(1) and R502.5(2).

Staff recommendation:  The IRC09 does not cover Florida specific provisions.  Recommend using the IRC09 provisions as the base text and then revise text to add  Florida specific provisions as stated above.

R602.2.1 Stud grade [IRC R602.2].  Studs…Table 602.2(5).

Renumber IRC sections as shown:

R602.2.2 [IRC R602.3.1] Stud size, height and spacing.

R602.2.3 [IRC R602.3.2] Top plate.

R602.2.4 [IRC R602.3.3] Bearing studs.

R602.2.5 [IRC R602.3.4] Bottom (sole) plate.

R602.2.6 [IRC R602.4] Interior load-bearing walls.

Table R602.2(1), [IRC 602.3(1)] Fastener Schedule for Structural Members

f. Reserved.

Table R602.2(2) [IRC R602.3(2)], Alternate Attachments

Overlap with Florida Specific - Structural TAC

FBC

Replaces Table R602.2(3) to read as shown. Resolve potential conflicts.

Table R602.2(3) [Table R602.3(3)]

REQUIREMENTS FOR WOOD STRUCTURAL PANEL WALL SHEATHING USED TO RESIST WIND PRESSURESa,b,c

| Minimum Nail |  | MINIMUM WOOD STRUCTURAL PANEL SPAN RATING | MINIMUM NOMINAL PANEL THICKNESS (inches) | MAXIMUM WALL STUD SPACING (inches) | Panel Nail Spacing |  | Maximum Wind Speed (mph) |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | Edges (inches oc) | Field (inches oc) | Wind Exposure Category |  |  |
| Size | Penetration |  |  |  |  |  | B | C | D |
| 6d Common (2.0″″ | 1.5 | 24/0 | 3/8 | 16 | 6 | 12 | 110 | 90 | 85 |
| 8d Common 4(2.5″0.131″) | 1.75 | 24/16 | 7/16 | 16 | 6 | 12 | 130 | 110 | 105 |
|  |  |  |  | 24 | 6 | 12 | 110 | 90 | 85 |

For SI: 1 inch = 25.4 mm, 1 mile per hour = 0.447 m/s.

a. Panel strength axis parallel or perpendicular to supports. Three-ply plywood sheathing with studs spaced more than 16 inches on center shall be applied with panel strength axis perpendicular to supports.

b. Table is based on wind pressures acting toward and away from building surfaces per Section R301.2. Lateral bracing requirements shall be in accordance with Section R602.2.10.

c. Wood Structural Panels with span ratings ofWall-16 or Wall-24 shall be permitted as an alternate to panels with a 24/0 span rating. Plywood siding rated 16 oc or 24 oc shall  be permitted as an alternate to panels with a 24/16 span rating. Wall-16 and Plywood siding 16 oc shall be used with studs spaced a maximum of 16 inches on center.

Staff recommendation:   Recommend limiting the scope of Table R602.2(3) to wind speed of 100 mph or less.  The IRC09 limits the use of IRC conventional construction requirements to 100 mph or less in hurricane-prone regions.

Table R602.2(4) [IRC Table R602.3(4)]. Allowable spans for Particleboard Wall Sheathing.

R602.2(5) [revised IRC Table R602.3(5)]. Size, height and Spacing of Wood Studs.

Figure R602.2(1) [IRC Figure R602.3(1)] Typical Wall, Floor and Roof Framing.

Figure R606.2(2) [IRC R602.3(2)]. Framing details.

TABLE R602.2.1 [IRC 602.3.1]  Maximum Allowable Length Of Wood Wall Studs Exposed To Wind Speeds Of 100 mph Or Less IN SEISMIC DESIGN CATEGORIES A, B, C, D0, D1 and D2 b, c [and continued figure]

Change Section R602.6 to read as follows:

R602.2.7 [IRC R602.6] Drilling and notching–studs. Drilling and notching of studs shall be in accordance with the following:

1. Notching. Any stud in an exterior wall or bearing partition may be cut or notched to a depth not exceeding 25 percent of its width. Studs in nonbearing partitions may be notched to a depth not to exceed 40 percent of a single stud width.

2. Drilling. Any stud may be bored or drilled, provided that the diameter of the resulting hole is no more than 60 percent of the stud width, the edge of the hole is no more than 5/8 inch (16 mm) to the edge of the stud, and the hole is not located in the same section as a cut or notch. Studs located in exterior walls or bearing partitions drilled over 40 percent and up to 60 percent shall also be doubled with no more than two successive doubled studs bored. See Figures R602.2.7(1) and R602.2.7(2).

Exception: Use of approved stud shoes is permitted when they are installed in accordance with the manufacturer’s recommendations.

.

R602.2.7.1 [R602.6.1] Drilling and notching of top plate. When piping or ductwork is placed in or partly in an exterior wall or interior load-bearing wall, necessitating cutting, drilling or notching of the top plate by more than 50 percent of its width, a galvanized metal tie not less than 0.054 inch thick (1.37 mm) (16 ga) and 11/2 inches (38 mm) wide shall be fastened across and to the plate at each side of the opening with not less than eight 10d (0.148 inch diameter) having a minimum length of 11/2 inches (38 mm) at each side or equivalent. The metal tie must extend a minimum of 6 inches past the opening. See Figure R602.2.7.1.

Exception: When the entire side of the wall with the notch or cut is covered by wood structural panel sheathing.

R602.2.8 [IRC R602.7] Headers. For header spans see Tables R502.2.5(1) and R502.2.5(2).

R602.2.8.1 [IRC 602.7.1] Wood structural panel box headers.  Wood structural panel box headers shall be constructed in accordance with Figure R602.2.8.1 and Table R602.2.8.1.

Table R602.2.8.1 [R602.7.2] Maximum Spans for Wood Structural Panel Box Headers.

Figure R602.2.8.1 [R602.7.2] Typical Wood Structural Panel Box Header Construction.

R602.2.9 [R602.9] Cripple walls. [No change to text except to reference Table R602.2(1)]

R602.10 Wall bracing. Buildings shall be braced in accordance with this section. Where a building, or portion thereof, does not comply with one or more of the bracing requirements in this section, those portions shall be designed and constructed in accordance with Section R301.1.

Exception: Detached one- and two-family dwellings located in Seismic Design Category C are exempt from the seismic bracing requirements of this section. Wind speed provisions for bracing shall be applicable to detached one- and two-family dwellings.

R602.2.10.1 Braced wall lines (IRCR602.10.1). Braced wall lines shall be provided in accordance with this section. The length of a braced wall line shall be measured as the distance between the ends of the wall line. The end of a braced wall line shall be considered to be either:

1. The intersection with perpendicular exterior walls or projection thereof,

2. The intersection with perpendicular braced wall lines.

The end of the braced wall line shall be chosen such that the maximum length results.

R602.2.10.1.1 Braced wall panels. Braced wall panels shall be constructed in accordance with the intermittent  racing methods specified in Section R602.2.10.2, or the continuous sheathing methods specified in Sections R602.2.10.4 and R602.2.10.5. Mixing of bracing method shall be permitted as follows:

1. Mixing bracing methods from story to story is permitted.

2. Mixing bracing methods from braced wall line to braced wall line within a story is permitted, except that continuous sheathing methods shall conform to the additional requirements of Sections R602.2.10.4 and R602.2.10.5.

3. Mixing bracing methods within a braced wall line is permitted only in Seismic Design Categories A and B, and detached dwellings in Seismic Design Category C. The length of required bracing for the braced wall line with mixed sheathing types shall have the higher bracing length requirement, in accordance with Tables R602.2.10.1.2(1) and R602.2.10.1.2(2), of all types of bracing used.

R602.2.10.1.2 Length of bracing. The length of bracing along each braced wall line shall be the greater of that required by the design wind speed and braced wall line spacing in accordance with Table R602.2.10.1.2(1) as adjusted by the factors in the footnotes or the Seismic Design Category and braced wall line length in accordance with Table R602.10.1.2(2) as adjusted by the factors in Table R602. 2.10.1.2(3) or braced wall panel location requirements of Section R602. 2.10.1.4. Only walls that are parallel to the braced wall line shall be counted toward the bracing requirement of that line, except angled walls shall be counted in accordance with Section R602. 2.10.1.3. In no case shall the minimum total length of bracing in a braced wall line, after all adjustments have been taken, be less than 48 inches (1219 mm) total.

R602.2.10.1.2.1 Braced wall panel uplift load path. Braced wall panels located at exterior walls that support roof rafters or trusses (including stories below top story) shall have the framing members connected in accordance with one of the following:

1. Fastening in accordance with Table R602. 2.3(1) where:

1.1. The basic wind speed does not exceed 90 mph (40 m/s), the wind exposure category is B, the roof pitch is 5:12 or greater, and the roof span is 32 feet (9754 mm) or less, or

1.2. The net uplift value at the top of a wall does not exceed 100 plf. The net uplift value shall be determined in accordance with Section R802.11 and shall be permitted to be reduced by 60 plf (86 N/mm) for each full wall above.

2. Where the net uplift value at the top of a wall exceeds 100 plf (146 N/mm), installing approved uplift framing connectors to provide a continuous load path from the top of the wall to the foundation. The net uplift value shall be as determined in Item 1.2 above.

3. Bracing and fasteners designed in accordance with accepted engineering practice to resist combined uplift and shear forces.

R602.2.10.1.3 Angled corners. At corners, braced wall lines shall be permitted to angle out of plane up to 45 degrees with a maximum diagonal length of 8 feet (2438 mm). When determining the length of bracing required, the length of each braced wall line shall be determined as shown in Figure R602.2.10.1.3. The placement of bracing for the braced wall lines shall begin at the point where the braced wall line, which contains the angled wall adjoins the adjacent braced wall line (Point A as shown in Figure R602.2.10.1.3).Where an angled corner is constructed at an angle equal to 45 degrees (0.79 rad) and the diagonal length is no more than 8 feet (2438 mm), the angled wall may be considered as part of either of the adjoining braced wall lines, but not both. Where the diagonal length is greater than 8 feet (2438 mm), it shall be considered its own braced wall line and be braced in accordance with Section R602. 2.10.1 and methods in Section R602. 2.10.2.

Change Tables as follows:

Table R602.2.10.1.2(1) Bracing Requirements Based On Wind Speed

Table R602.2.10.1.2(2) Bracing Requirements Based On Seismic Design Category (As A Function Of Braced Wall Line Length  Reserved.

TABLE R602.2.10.1.2(3) Adjustment Factors To The Length Of Required Seismic Wall Bracing a  Reserved.

R602.2.10.1.4.1 Braced wall panel location in Seismic Design Categories D0, D1 and D2. Reserved.

Figure R602.2.10.1.4.1 Braced Wall Panels at Ends of Braced Wall Lines in Seismic Design Categories D0, D1 AND D2.  Reserved.

R602.2.10.1.5 Braced wall line spacing for Seismic Design Categories D0, D1 and D2. Reserved.

Table R602.2.10.1.5 Adjustments of Bracing Length for Braced Wall Lines Greater Than 25 Feet. Reserved.

R602.2.10.2 Intermittent braced wall panel construction methods. The construction of intermittent braced wall panels shall be in accordance with one of the methods listed in Table R602.2.10.2.

R602. 2.10.2.1 Intermittent braced wall panel interior finish material. Intermittent braced wall panels shall have gypsum wall board installed on the side of the wall opposite the bracing material. Gypsum wall board shall be not less than 1/2 inch (12.7 mm) in thickness and be fastened in accordance with Table R702.3.5 for interior gypsum wall board.

Exceptions:

1. Wall panels that are braced in accordance with Methods GB, ABW, PFG and PFH.

2. When an approved interior finish material with an in-plane shear resistance equivalent to gypsum board is installed.

3. For Methods DWB, WSP, SFB, PBS, PCP and HPS, omitting gypsum wall board is permitted provided the length of bracing in Tables R602.10.1.2(1) and R602.10.1.2(2) is multiplied by a factor of 1.5.

R602.2.10.2.2 Adhesive attachment of sheathing in Seismic Design Categories C, D0, D1 and D2. Reserved. Adhesive attachment of wall sheathing shall not be permitted in Seismic Design Categories C, D0, D1 and D2.

R602.2.10.3  Minimum length of braced panels. For Methods DWB, WSP, SFB, PBS, PCP and HPS, each braced wall panel shall be at least 48 inches (1219 mm) in length, covering a minimum of three stud spaces where studs are spaced 16 inches (406 mm) on center and covering a minimum of two stud spaces where studs are spaced 24 inches (610 mm) on center. For Method GB, each braced wall panel and shall be at least 96 inches (2438 mm) in length where applied to one face of a braced wall panel and at least 48 inches (1219 mm) where applied to both faces. For Methods DWB, WSP, SFB, PBS, PCP and HPS, for purposes of computing the length of panel bracing required in Tables R602.2.10.1.2(1) and R602.10.1.2(2), the effective length of the braced wall panel shall be equal to the actual length of the panel. When Method GB panels are applied to only one face of a braced wall panel, bracing lengths required in Tables R602.2.10.1.2(1) and R602.10.1.2(2) for Method GB shall be doubled.

Exceptions:

1. Lengths of braced wall panels for continuous sheathing methods shall be in accordance with Table R602.2.10.4.2.

2. Lengths of Method ABW panels shall be in accordance with Sections R602.2.10.3.2.

3. Length of Methods PFH and PFG panels shall be in accordance with Section R602.2.10.3.3 and R602.2.10.3.4 respectively.

4. Reserved. For Methods DWB, WSP, SFB, PBS, PCP and HPS in Seismic Design Categories A, B, and C:  Panels between 36 inches (914 mm)and 48 inches (1219 mm) in length shall be permitted to count towards the required length of bracing in Tables R602.2.10.1.2(1) and R602.2.10.1.2(2), and the effective contribution shall comply with Table R602.2.10.3.

R602.2.10.3.1 Adjustment of length of braced panels. When story height (H), measured in feet, exceeds 10 feet (3048 mm), in accordance with Section R301.3, the minimum length of braced wall panels specified in Section R602.2.10.3 shall be increased by a factor H/10. See Table R602.2.10.3.1. Interpolation is permitted.

R602.2.10.3.2 Method ABW: Alternate braced wall panels. Method ABW braced wall panels constructed in accordance with one of the following provisions shall be permitted to replace each 4 feet (1219 mm) of braced wall panel as required by Section R602. 2.10.3. The maximum height and minimum length and hold-down force of each panel shall be in accordance with Table R602. 2.10.3.2:

1. In one-story buildings, each panel shall be installed in accordance with Figure R602.2.10.3.2. The hold-down device shall be installed in accordance with the manufacturer’s recommendations. The panels shall be supported directly on a foundation or on floor framing supported directly on a foundation which is continuous across the entire length of the braced wall line.

2. In the first story of two-story buildings, each braced wall panel shall be in accordance with Item 1 above, except that the wood structural panel sheathing edge nailing spacing shall be installed on both faces shall not exceed 4 inches (102 mm) on center, at least three anchor bolts shall be placed at one-fifth points.

TABLE R602.2.10.3.1 Minimum Length Requirements for Braced Wall Panels. [Delete SDC A,B,C,D….line]

TABLE R602.2.10.3.2 Minimum Length Requirements and Hold-Down Forced for Method ABW Braced Wall Panels. [Delete lines “SDC A – D]

For SI: 1 inch = 25.4 mm, 1 foot = 305 mm, 1 pound = 4.448 N.

a. NP = Not Permitted. Maximum height of 10 feet.

R602.2.10.3.3 [was R602.10.6.2] Method PFH: Portal frame with hold-downs. Method PFH braced wall panels constructed in accordance with one of the following provisions are also permitted to replace each 4 feet (1219 mm) of braced wall panel as required by Section R602.2.10.3 for use adjacent to a window or door opening with a full-length header:

1. Each panel shall be fabricated in accordance with Figure R602.2.10.3.3. The wood structural panel sheathing shall extend up over the solid sawn or glued-laminated header and shall be nailed in accordance with Figure R602.2.10.3.3. A spacer, if used with a built-up header, shall be placed on the side of the built-up beam opposite the wood structural panel sheathing. The header shall extend between the inside faces of the first full-length outer studs of each panel and the bearing studs at the other end of the opening. One anchor bolt not less than 5/8-inch-diameter (16 mm) and installed in accordance with Section R403.1.6 shall be provided in the center of each sill plate. The hold-down devices shall be an embedded-strap type, installed in accordance with the manufacturer’s recommendations. The panels shall be supported directly on a foundation which is continuous across the entire length of the braced wall line. The foundation shall be reinforced as shown on Figure R602. 2.10.3.2. This reinforcement shall be lapped not less than 15 inches (381 mm) with the reinforcement required in the continuous foundation located directly under the braced wall line.

2. In the first story of two-story buildings, each wall panel shall be braced in accordance with item 1 above, except that each panel shall have a length of not less than 24 inches (610 mm).

R602.2.10.3.4 Method PFG: at garage door openings in Seismic Design Categories A,B and C . Reserved. Where supporting a roof or one story and a roof, alternate braced wall panels constructed in accordance with the following provisions are permitted on either side of garage door openings. For the purpose of calculating wall bracing amounts to satisfy the minimum requirements of Table R602. 2.10.1.2(1), the length of the alternate braced wall panel shall be multiplied by a factor of 1.5.

1. Braced wall panel length shall be a minimum of 24 inches (610 mm) and braced wall panel height shall be a maximum of 10 feet (3048 mm).

2. Braced wall panel shall be sheathed on one face with a single layer of 7/16-inch-minimum (11 mm) thickness wood structural panel sheathing attached to framing with 8d common nails at 3 inches (76 mm) on center in accordance with Figure R602.2.10.3.4.

3. The wood structural panel sheathing shall extend up over the solid sawn or glued-laminated header and shall be nailed to the header at 3 inches (76 mm) on center grid in accordance with Figure R602. 2.10.3.4.

4. The header shall consist of a minimum of two solid sawn 212s (51 by 305 mm) or a 3 inches 11.25 inch (76 by 286 mm) glued-laminated header. The header shall extend between the inside faces of the first full-length outer studs of each panel in accordance with Figure R602. 2.10.3.4. The clear span of the header between the inner studs of each panel shall be not less than 6 feet (1829 mm) and not more than 18 feet (5486 mm) in length.

5. A strap with an uplift capacity of not less than 1,000 pounds (4448 N) shall fasten the header to the side of the inner studs opposite the sheathing face. Where building is located in Wind Exposure Categories C or D, the strap uplift capacity shall be in accordance with Table R602.2.10.4.1.1.

6. A minimum of two bolts not less than 1/2-inch (12.7 mm) diameter shall be installed in accordance with Section R403.1.6. A 3/16-inch by 2 1/2-inch (4.8 by 63 by 63 mm) by 2 1/2-inch steel plate washer is installed between the bottom plate and the nut of each bolt.

7. Braced wall panel shall be installed directly on a foundation.

8. Where an alternate braced wall panel is located only on one side of the garage opening, the header shall be connected to a supporting jack stud on the opposite side of the garage opening with a metal strap with an uplift capacity of not less than 1,000 pounds. Where that supporting jack stud is not part of a braced wall panel assembly, another 1,000 pounds (4448 N) strap shall be installed to attach  the supporting jack stud to the foundation.

FIGURE R602.2.10.3.4 Method PFG Portal Frame at Garage Door Openings in Seismic Categories A, B and C.  Reserved.

R602.2.10.4 Continuous sheathing. Braced wall lines with continuous sheathing shall be constructed in accordance with this section. All braced wall lines along exterior walls

on the same story shall be continuously sheathed.

Exception:  Reserved Within Seismic Design Categories A, B and C or in regions where the basic wind speed is less than or equal to 100 mph (45 m/s), other bracing methods prescribed by this code shall be permitted on other braced wall lines on the same story level or on any braced wall line on different story levels of the building.

R602.2.10.4.4 Continuously sheathed braced wall panel location and corner construction. For all continuous sheathing methods, full-height braced wall panels complying with the length requirements of Table R602. 2.10.4.2 shall be located at each end of a braced wall line with continuous sheathing and at least every 25 feet (7620 mm) on center. A minimum 24 inch (610 mm) wood structural panel corner return shall be provided at both ends of a braced wall line with continuous sheathing in accordance with Figures R602. 2.10.4.4(1) and R602. 2.10.4.4(2). In lieu of the corner return, a hold-down device with a minimum up lift design value of 800 pounds (3560 N) shall be fastened to the corner stud and to the foundation or framing below in accordance with Figure R602. 2.10.4.4(3).

Exception: The first braced wall panel in Seismic Design Categories A, B and C

Change Table R602.2.10.4.2 as follows:

Make changes to Figure R602.2.104.4(1).

R602. 2.10.5.3 Braced wall panel location and corner construction. A braced wall panel shall be located at each end of a continuously-sheathed braced wall line. A minimum 32-inch (813 mm) structural fiberboard sheathing panel corner return shall be provided at both ends of a continuously-sheathed braced wall line in accordance with Figure R602. 2.10.4.4(1) In lieu of the corner return, a hold-down device with a minimum uplift design value of 800 pounds (3560 N) shall be fastened to the corner stud and to the foundation or framing below in

accordance with Figure R602. 2.10.4.4(3).

Exception:  Reserved. The first braced wall panel …in Seismic Design Categories A, B and C provided one of the following is satisfied:….

R602.2.10.5.4 Continuously sheathed braced wall lines. Where a continuously-sheathed braced wall line is used in Seismic Design Categories D0, D1 and D2 or regions where the basic wind speed exceeds 100 miles per hour (45 m/s), the braced wall line shall be designed in accordance with accepted engineering practice and the provisions of the Florida International Building Code. Also, all other exterior braced wall lines in the same story shall be continuously

sheathed.

R602.2.10.6.1 Braced wall panel connections for Seismic Design Categories D0, D1 andD2.  Reserved.

Change R602.2.10.6 as follows:

R602.2.10.6 Alternate braced wall panel construction methods. Alternate braced wall panels shall be constructed in accordance with Sections R602.2.10.6.1 and R602.2.10.2.

R602.2.10.6.1 Alternate braced wall panels. Alternate braced wall lines constructed in accordance with one of the following provisions shall be permitted to replace each 4 feet (1219 mm) of braced wall panel as required by Section R602.2.10.4. The maximum height and minimum width of each panel shall be in accordance with Table R602.2.10.6:

1. In one-story buildings, each panel shall have a length of not less than 2 feet, 8 inches (813 mm) and a height of not more than 10 feet (3048 mm). Each panel shall be sheathed on one face with 3 / 8-inch minimum- thickness (9.5 mm) wood structural panel sheathing nailed with 8d common or galvanized box nails in accordance with Table R602.2(1) and blocked at all wood structural panel sheathing edges. Two anchor bolts installed in accordance with Figure R403.1(1) shall be provided in each panel. Anchor bolts shall be placed at panel quarter points. Each panel end stud shall have a tie-down device fastened to the foundation, capable of providing an uplift capacity in accordance with Table R602.2.10.6 of at least 1,800 pounds (816.5 kg). The tie-down device shall be installed in accordance with the manufacturer’s recommendations. The panels shall be supported directly on a foundation or on floor framing supported directly on a foundation which is continuous across the entire length of the braced wall line. This foundation shall be reinforced with not less than one No. 4 bar top and bottom. When the continuous foundation is required to have a depth greater than 12 inches (305 mm), a minimum 12-inch-by-12-inch (305 mm by 305 mm) continuous footing or turned down slab edge is permitted at door openings in the braced wall line. This continuous footing or turned down slab edge shall be reinforced with not less than one No. 4 bar top and bottom. This reinforcement shall be lapped 15 inches (381 mm) with the reinforcement required in the continuous foundation located directly under the braced wall line.

2. In the first story of two-story buildings, each braced wall panel shall be in accordance with Item 1 above, except that the wood structural panel sheathing shall be provided on both faces, sheathing edge nailing spacing shall not exceed four inches (102 mm) on center, at least three anchor bolts shall be placed at one-fifth points, and tie-down device uplift capacity shall not be less than 3,000 pounds (1360.8 kg).

Add R602.2.10.6.2 as follows:

R602.2.10.6.2 Alternate braced wall panel adjacent to a door or window opening. Alternate braced wall panels constructed in accordance with one of the following provisions are also permitted to replace each 4 feet (1219 mm) of braced wall panel as required by Section R602.2.10.4 for use adjacent to a window or door opening with a full-length header:

1. In one-story buildings, each panel shall have a length of not less than 16 inches (406 mm) and a height of not more than 10 feet (3048 mm). Each panel shall be sheathed on one face with a single layer of 3/8-inch-minimum-thickness (10 mm) wood structural panel sheathing nailed with 8d common or galvanized box nails in accordance with Figure R602.2.10.6.2. The wood structural panel sheathing shall extend up over the solid sawn or glued-laminated header and shall be nailed in accordance with Figure R602.2.10.6.2. Use of a built-up header consisting of at least two 2 x 12s and fastened in accordance with Table R602.2(1) shall be permitted. A spacer, if used, shall be placed on the side of the built-up beam opposite the wood structural panel sheathing. The header shall extend between the inside faces of the first full-length outer studs of each panel. The clear span of the header between the inner studs of each panel shall be not less than 6 feet (1829 mm) and not more than 18 feet (5486 mm) in length. A strap with an uplift capacity of not less than 1000 pounds (4448 N) shall fasten the header to the side of the inner studs opposite the sheathing. One anchor bolt not less than 5/8-inch-diameter (16 mm) and installed in accordance with Section R403.1.6 shall be installed in the center of each sill plate. The studs at each end of the panel shall have a tie-down device fastened to the foundation with an uplift capacity of not less than 4,200 pounds (18 683 N).

Where a panel is located on one side of the opening, the header shall extend between the inside face of the first full-length stud of the panel and the bearing studs at the other end of the opening. A strap with an uplift capacity of not less than 1000 pounds (4448 N) shall fasten the header to the bearing studs. The bearing studs shall also have a tie-down device fastened to the foundation with an uplift capacity of not less than 1000 pounds (4448 N).

The tie-down devices shall be an embedded strap type, installed in accordance with the manufacturer’s recommendations. The panels shall be supported directly on a foundation which is continuous across the entire length of the braced wall line. The foundation shall be reinforced with not less than one No. 4 bar top and bottom.

Where the continuous foundation is required to have a depth greater than 12 inches (305 mm), a minimum 12-inch-by-12-inch (305 mm by 305 mm) continuous footing or turned down slab edge is permitted at door openings in the braced wall line. This continuous footing or turned down slab edge shall be reinforced with not less than one No. 4 bar top and bottom. This reinforcement shall be lapped not less than 15 inches (381 mm) with the reinforcement required in the continuous foundation located directly under the braced wall line.

2. In the first story of two-story buildings, each wall panel shall be braced in accordance with Item 1 above, except that each panel shall have a length of not less than 24 inches (610 mm).

R602.2.10.6.2 Connections to roof framing. Exterior braced wall panels shall be connected to roof framing as follows.

1. Parallel rafters or roof trusses shall be attached to the top plates of braced wall panels in accordance with Table R602.3(1).

2. For SDC A, B and C and wind speeds less than 100 miles per hour (45 m/s), where the distance from the top of the rafters or roof trusses and perpendicular top plates is 91/4 inches (235 mm) or less, the rafters or roof trusses shall be connected to the top plates of braced wall lines in accordance with Table R602.3(1) and blocking need not be installed. Where the distance from the top of the rafters and perpendicular top plates is between 9 1/4 inches (235 mm) and 15 1/4 inches (387 mm) the rafters shall be connected to the top plates of braced wall panels with blocking in accordance with Figure R602.2.10.6.2(1) and attached in accordance with Table R602.3(1). Where the distance from the top of the roof trusses and perpendicular top plates is between 91/4 inches (235 mm) and 151/4 inches (387 mm)

the roof trusses shall be connected to the top plates of braced wall panels with blocking in accordance with Table R602.3(1).

3. For SDCD0,D1 andD2 or wind speeds of 100 miles per hour (45 m/s) or greater, where the distance between the top of rafters or roof trusses and perpendicular top plates is 151/4 inches (387 mm) or less, rafters or roof trusses shall be connected to the top plates of braced wall panels with blocking in accordance with Figure R602.2.10.6.2(1) and attached in accordance with Table R602.3(1).

4. For all seismic design categories and wind speeds, where the distance between the top of rafters or roof trusses and perpendicular top plates exceeds 15 1/4 inches (387 mm), perpendicular rafters or roof trusses shall be connected to the top plates of braced wall panels in accordance with one of the following methods:

4.1. In accordance with Figure R602.2.10.6.2(2),

4.2. In accordance with Figure R602.2.10.6.2(3),

4.3. With full height engineered blocking panels designed for values listed in American Forest and Paper Association (AF&PA) Wood Frame Construction Manual for One- and Two-Family Dwellings (WFCM). Both the roof and floor sheathing shall be attached to the blocking panels in accordance with Table R602.2.3(1).

4.4. Designed in accordance with accepted engineering methods. Lateral support for the rafters and ceiling joists shall be provided in accordance with Section R802.8. Lateral support for trusses shall be provided in accordance with Section R802.10.3. Ventilation shall be provided in accordance with Section R806.1.

Change R602.2.10.7 as follows:

R602.2.10.87 Panel joints. All vertical joints of panel sheathing shall occur over, and be fastened to, common studs. Horizontal joints in braced wall panels shall occur over, and be fastened to common blocking of a minimum of 1 1/2 inch (38 mm) thickness.

Exceptions:

1. Blocking at horizontal joints shall not be required in wall segments that are not counted as braced wall panels.

2. Where the bracing length provided is at least twice the minimum length required by Tables R602.10.1.2(1) and R602.10.1.2(2) blocking at horizontal joints shall not be required in braced wall panels constructed using Methods WSP, SFB, GB, PBS or HPS.

3. When Method GB panels are installed horizontally, blocking of horizontal joints is not required.

R602.2.10.7 Braced wall panel support. Braced wall panel support shall be provided as follows:

1. Cantilevered floor joists, supporting braced wall lines, shall comply with Section R502.3.3. Solid blocking shall be provided at the nearest bearing wall location. In Seismic Design Categories A, B and C, where the cantilever is not more than 24 inches (610 mm), a full height rim joist instead of solid blocking shall be provided.

2. Elevated post or pier foundations supporting braced wall panels shall be designed in accordance with accepted engineering practice.

3. Masonry stem walls with a length of 48 inches (1220 mm) or less supporting braced wall panels shall be reinforced in accordance with Figure R602. 2.10.7. Masonry stem walls with a length greater than 48 inches (1220 mm) supporting braced wall panels shall be constructed in accordance with Section R403.1 Braced wall panels constructed in accordance with Sections R602.2.10.3.2 and R602.2.10.3.3 shall not be attached to masonry stem walls.

R602.2.10.7.1 Braced wall panel support for Seismic Design Category D2.  Reserved.

R602.2.10.9 Cripple wall bracing.  Reserved.

R602.2.10.9.1 Cripple wall bracing in Seismic Design Categories D0, D1 and D2.  Reserved.

R602.2.10.9.2 Redesignation of cripple walls.  Reserved.

R602.2.11 Wall anchorage. Braced wall line sills shall be anchored to concrete or masonry foundations in  accordance with Sections R403.1.6 and R602.11.1.

602.2.11.1 Wall anchorage for all buildings in Seismic Design Categories D0, D1 and D2 and townhouses in Seismic Design Category C.   Reserved.

R602.2.11.2 Stepped foundations in Seismic Design Categories D0, D1 and D2.  Reserved.

R602.2.12 Wall bracing and stone and masonry veneer. Where stone and masonry veneer is installed in accordance with Section R703.7, wall bracing shall comply with this section. For all buildings in Seismic Design Categories A, B and C, …foundations.

R602.2.12.1 Seismic Design Categories D0, D1 and D2.  Reserved.

TABLE R602.2.12(1).  STONE OR MASONRY VENEER WALL BRACING REQUIREMENTS, WOOD OR STEEL FRAMING, SEISMIC DESIGN CATEGORIES A, B and C  Reserved.

TABLE R602.2.12(2). STONE OR MASONRY VENEER WALL BRACING REQUIREMENTS, ONE- AND TWO-FAMILY DETACHED DWELLINGS, SEISMIC DESIGN CATEGORIES D0, D1 and D2  Reserved.

R602.3  Add section to read as shown:

R602.3 Design and construction where wind speed is 100 miles per hour (45 m/s) or greater. Exterior walls of light-frame wood construction shall be designed and constructed  in accordance with the provisions of Section  R301.2.1.1 and R602.1.1.

R603.1.1 Applicability limits. The provisions of this section shall control the construction of exterior cold-formed steel wall framing and interior load-bearing cold-formed steel wall framing for buildings not more than 60 feet (18 288 mm) long perpendicular to the joist or truss span, not more than 40 feet (12 192 mm) wide parallel to the joist or truss span, and less than or equal to three stories above grade plane. All exterior walls installed in accordance with the provisions of this section shall be considered as load-bearing walls. Cold-formed steel walls constructed in accordance with the provisions of this section shall be limited to sites subjected to a maximum design wind speed of 110 miles per hour (49 m/s) Exposure B or C and a maximum ground snowload of 70 pounds per square foot (3.35 kPa).

Change R603.2 as follows:

R603.2 Structural framing. Load-bearing steel wall framing members shall comply with Figure R603.2(1) and with the dimensional and minimum thickness requirements specified in Tables R603.2(1) and R603.2(2). Tracks shall comply with Figure R603.2(2) and shall have a minimum flange width of 1 ¼ inches (32 mm). The maximum inside bend radius for members shall be the greater of 3/32 inch (2.4 mm) minus half the base steel thickness or 1.5  the base steel thickness.

R603.2.1 No change.

R603.3.2Minimum stud sizes. Cold-formed steel walls shall be constructed in accordance with Figures R603.3.1(1), R603.3.1(2), or R603.3.1(3), as applicable. Exterior wall stud size and thickness shall be determined in accordance with the limits set forth in Tables R603.3.2(2) through R603.3.2(31). Interior load-bearing wall stud size and thickness shall be determined in accordance with the limits set forth in Tables R603.3.2(2) throughR603.3.2(31) based upon an 85 miles per hour (38 m/s) Exposure A/B wind value and the building width, and stud spacing and snow load, as appropriate. Fastening requirements shall be in accordance with Section R603.2.4 and Table R603.3.2(1). Top and bottom tracks shall have the same minimum thickness as the wall studs. Exterior wall studs shall be permitted to be reduced to the next thinner size, as shown in Tables R603.3.2(2) through R603.3.2(31), but not less than 33 mils (0.84 mm) ,where both of the following conditions exist:

1. Minimum of 1/2 inch (12.7 mm) gypsum board is installed and fastened in accordance with Section R702 on the interior surface.

2. Wood structural sheathing panels of minimum 7/16 inch (11 mm) thick oriented strand board or 15/32 inch (12 mm) thick plywood is installed and fastened in accordance with Section R603.9.1 and Table R603.3.2(1) on the outside surface.

Interior load-bearing walls shall be permitted to be reduced to the next thinner size, as shown in Tables R603.3.2(2) through R603.3.2(31), but not less than 33 mils (0.84 mm), where a minimum of 1/2 inch (12.7 mm) gypsum board is installed and fastened in accordance with Section R702 on both sides of the wall. The tabulated stud thickness for load bearing walls shall be used when the attic load is 10 pounds per square feet (480 Pa) or less. A limited attic storage load of 20 pounds per square feet (960 Pa) shall be permitted provided that the next higher snow load column is used to select the stud size from Tables R603.3.2(2) through R603.3.2(31).

For two-story buildings, the tabulated stud thickness for walls supporting one floor, roof and ceiling shall be used when second floor live load is 30 pounds per square feet (1440 Pa). Second floor live loads of 40 psf (1920 pounds per square feet) shall be permitted provided that the next higher snow load column is used to select the stud size from Tables R603.3.2(2) through R603.3.2(21).

For three-story buildings, the tabulated stud thickness for walls supporting one or two floors, roof and ceiling shall be used when the third floor live load is 30 pounds per square feet (1440 Pa). Third floor live loads of 40 pounds per square feet (1920 Pa) shall be permitted provided that the next higher snow load column is used to select the stud size from Tables R603.3.2(22) through R603.3.2(31).

TABLE R603.3.2(2)

24-FOOT-WIDE BUILDING SUPPORTING ROOF AND CEILING ONLYa, b, c

33 ksi STEEL  (revise to remove snow load)

TABLE R603.3.2(3)

24-FOOT-WIDE BUILDING SUPPORTING ROOF AND CEILING ONLYa,b,c

50 ksi STEEL   (revise to remove snow load)

TABLE R603.3.2(4)

28-FOOT-WIDE BUILDING SUPPORTING ROOF AND CEILING ONLYa,b,c

33 ksi STEEL   (revise to remove snow load)

TABLE R603.3.2(5)

28-FOOT-WIDE BUILDING SUPPORTING ROOF AND CEILING ONLYa,b,c

50 ksi STEEL   (revise to remove snow load)

TABLE R603.3.2(6)

32-FOOT-WIDE BUILDING SUPPORTING ROOF AND CEILING ONLYa,b,c

33 ksi STEEL   (revise to remove snow load)

TABLE R603.3.2(7)

32-FOOT-WIDE BUILDING SUPPORTING ROOF AND CEILING ONLYa,b,c

50 ksi STEEL   (revise to remove snow load)

TABLE R603.3.2(8)

36-FOOT-WIDE BUILDING SUPPORTING ROOF AND CEILING ONLYa,b,c

33 ksi STEEL   (revise to remove snow load)

TABLE R603.3.2(9)

36-FOOT-WIDE BUILDING SUPPORTING ROOF AND CEILING ONLYa,b,c

50 ksi STEEL   (revise to remove snow load)

TABLE R603.3.2(10)

40-FOOT-WIDE BUILDING SUPPORTING ROOF AND CEILING ONLYa,b,c

33 ksi STEEL   (revise to remove snow load)

TABLE R603.3.2(11)

40-FOOT-WIDE BUILDING SUPPORTING ROOF AND CEILING ONLYa,b,c

50 ksi STEEL   (revise to remove snow load)

TABLE R603.3.2(12)

24-FOOT-WIDE BUILDING SUPPORTING ONE FLOOR, ROOF AND CEILINGa,b,c

33 ksi STEEL   (revise to remove snow load)

TABLE R603.3.2(13)

24-FOOT-WIDE BUILDING SUPPORTING ONE FLOOR, ROOF AND CEILINGa,b,c

50 ksi STEEL   (revise to remove snow load)

TABLE R603.3.2(14)

28-FOOT-WIDE BUILDING SUPPORTING ONE FLOOR, ROOF AND CEILINGa,b,c

33 ksi STEEL   (revise to remove snow load)

TABLE R603.3.2(15)

28-FOOT-WIDE BUILDING SUPPORTING ONE FLOOR, ROOF AND CEILINGa,b,c

50 ksi STEEL   (revise to remove snow load)

TABLE R603.3.2(16)

32-FOOT-WIDE BUILDING SUPPORTING ONE FLOOR, ROOF AND CEILINGa,b,c

33 ksi STEEL   (revise to remove snow load)

TABLE R603.3.2(17)

32-FOOT-WIDE BUILDING SUPPORTING ONE FLOOR, ROOF AND CEILINGa,b,c

50 ksi STEEL  (revise to remove snow load)

TABLE R603.3.2(18)

36-FOOT-WIDE BUILDING SUPPORTING ONE FLOOR, ROOF AND CEILINGa,b,c

33 ksi STEEL   (revise to remove snow load)

TABLE R603.3.2(19)

36-FOOT-WIDE BUILDING SUPPORTING ONE FLOOR, ROOF AND CEILINGa,b,c

50 ksi STEEL   (revise to remove snow load)

TABLE R603.3.2(20)

40-FOOT-WIDE BUILDING SUPPORTING ONE FLOOR, ROOF AND CEILINGa,b,c

33 ksi STEEL   (revise to remove snow load)

TABLE R603.3.2(21)

40-FOOT-WIDE BUILDING SUPPORTING ONE FLOOR, ROOF AND CEILINGa,b,c

50 ksi STEEL   (revise to remove snow load)

TABLE R603.3.2(22)

24-FOOT-WIDE BUILDING SUPPORTING TWO FLOORS, ROOF AND CEILINGa,b,c

33 ksi STEEL   (revise to remove snow load)

TABLE R603.3.2(23)

24-FOOT-WIDE BUILDING SUPPORTING TWO FLOORS, ROOF AND CEILINGa,b,c

50 ksi STEEL   (revise to remove snow load)

TABLE R603.3.2(24)

28-FOOT-WIDE BUILDING SUPPORTING TWO FLOORS, ROOF AND CEILINGa,b,c

33 ksi STEEL   (revise to remove snow load)

TABLE R603.3.2(25)

28-FOOT-WIDE BUILDING SUPPORTING TWO FLOORS, ROOF AND CEILINGa,b,c

50 ksi STEEL   (revise to remove snow load)

TABLE R603.3.2(26)

32-FOOT-WIDE BUILDING SUPPORTING TWO FLOORS, ROOF AND CEILINGa,b,c

33 ksi STEEL   (revise to remove snow load)

TABLE R603.3.2(27)

32-FOOT-WIDE BUILDING SUPPORTING TWO FLOORS, ROOF AND CEILINGa,b,c

50 ksi STEEL   (revise to remove snow load)

TABLE R603.3.2(28)

36-FOOT-WIDE BUILDING SUPPORTING TWO FLOORS, ROOF AND CEILINGa,b,c

33 ksi STEEL   (revise to remove snow load)

TABLE R603.3.2(29)

36-FOOT-WIDE BUILDING SUPPORTING TWO FLOORS, ROOF AND CEILINGa,b,c

50 ksi STEEL   (revise to remove snow load)

TABLE R603.3.2(30)

40-FOOT-WIDE BUILDING SUPPORTING TWO FLOORS, ROOF AND CEILINGa,b,c

3 ksi STEEL   (revise to remove snow load)

TABLE R603.3.2(31)

40-FOOT-WIDE BUILDING SUPPORTING TWO FLOORS, ROOF AND CEILINGa,b,c

50 ksi STEEL   (revise to remove snow load)

TABLE R603.3.2.1(1)

ALL BUILDING WIDTHS

GABLE ENDWALLS 8, 9 OR 10 FEET IN HEIGHTa,b,c

33 ksi STEEL

For SI: 1 inch = 25.4, 1 foot = 304.8 mm, 1 mil = 0.0254 mm, 1 mile per hour = 0.447 m/s, 1 pound per square foot = 0.0479kPa, 1 ksi = 6.895 MPa.

a. Deflection criterion L/240.

b. Design load assumptions:

Ground snow load is 70 psf. Roof and ceiling dead load is 12 psf.  Floor dead load is 10 psf. Floor live load is 40 psf. Attic dead load is 10 psf.

c. Building width is in the direction of horizontal framing members supported by the wall studs.

TABLE R603.3.2.1(2)

ALL BUILDING WIDTHS

GABLE ENDWALLS 8, 9 OR 10 FEET IN HEIGHTa,b,c

50 ksi STEEL

For SI: 1 inch = 25.4, 1 foot = 304.8 mm, 1 mil = 0.0254 mm, 1 mile per hour = 0.447 m/s, 1 pound per square foot = 0.0479kPa, 1 ksi = 6.895 MPa.

a. Deflection criterion L/240.

b. Design load assumptions:

Ground snow load is 70 psf. Roof and ceiling dead load is 12 psf. Floor dead load is 10 psf. Floor live load is 40 psf. Attic dead load is 10 psf.

c. Building width is in the direction of horizontal framing members supported by the wall studs.

TABLE R603.3.2.1(3)

ALL BUILDING WIDTHS

GABLE ENDWALLS OVER 10 FEET IN HEIGHTa,b,c

33 ksi STEEL

For SI: 1 inch = 25.4, 1 foot = 304.8 mm, 1 mil = 0.0254 mm, 1 mile per hour = 0.447 m/s, 1 pound per square foot = 0.0479kPa, 1 ksi = 6.895 MPa.

a. Deflection criterion L/240.

b. Design load assumptions:

Ground snow load is 70 psf. Roof and ceiling dead load is 12 psf. Floor dead load is 10 psf. Floor live load is 40 psf. Attic dead load is 10 psf.

c. Building width is in the direction of horizontal framing members supported by the wall studs.

TABLE R603.3.2.1(4)

ALL BUILDING WIDTHS

GABLE ENDWALLS OVER 10 FEET IN HEIGHTa,b,c

50 ksi STEEL

For SI: 1 inch = 25.4, 1 foot = 304.8 mm, 1 mil = 0.0254 mm, 1 mile per hour = 0.447 m/s, 1 pound per square foot = 0.0479kPa, 1 ksi = 6.895 MPa.

a. Deflection criterion L/240.

b. Design load assumptions:

Ground snow load is 70 psf. Roof and ceiling dead load is 12 psf. Floor dead load is 10 psf. Floor live load is 40 psf. Attic dead load is 10 psf.

c. Building width is in the direction of horizontal framing members supported by the wall studs.

TABLE R603.6(1)

BOX-BEAM HEADER SPANS

Headers Supporting Roof and Ceiling Only (33 ksi steel) a, b  Reserved.

TABLE R603.6(2)

BOX-BEAM HEADER SPANS

Headers Supporting Roof and Ceiling Only (50 ksi steel) a, b  Reserved.

TABLE R603.6(3)

BOX-BEAM HEADER SPANS

Headers Supporting Roof and Ceiling Only (33 ksi steel) a, b  Reserved.

TABLE R603.6(4)

BOX-BEAM HEADER SPANS

Headers Supporting Roof and Ceiling Only (50 ksi steel) a, b  Reserved.

TABLE R603.6(5)

BOX-BEAM HEADER SPANS

Headers Supporting One Floor, Roof and Ceiling (33 ksi steel) a, b  Reserved.

TABLE R603.6(6)

BOX-BEAM HEADER SPANS

Headers Supporting One Floor, Roof and Ceiling (50 ksi steel) a, b  Reserved.

TABLE R603.6(7)

BOX-BEAM HEADER SPANS

Headers Supporting One Floor, Roof and Ceiling (33 ksi steel) a, b  Reserved.

TABLE R603.6(8)

BOX-BEAM HEADER SPANS

Headers Supporting One Floor, Roof and Ceiling (50 ksi steel) a, b  Reserved.

TABLE R603.6(9)

BOX-BEAM HEADER SPANS

Headers Supporting Two Floors, Roof and Ceiling (33 ksi steel)a  Reserved.

TABLE R603.6(10)

BOX-BEAM HEADER SPANS

Headers Supporting Two Floors, Roof and Ceiling (50 ksi steel) a, b  Reserved.

TABLE R603.6(11)

BOX-BEAM HEADER SPANS

Headers Supporting Two Floors, Roof and Ceiling (33 ksi steel) a, b  Reserved.

TABLE R603.6(12)

BOX-BEAM HEADER SPANSa,b,c

Headers Supporting Two Floors, Roof and Ceiling (50 ksi steel) a, b  Reserved.

TABLE R603.6(13)

BACK-TO-BACK HEADER SPANS

Headers Supporting Roof and Ceiling Only (33 ksi steel) a, b  Reserved.

TABLE R603.6(14)

BACK-TO-BACK HEADER SPANS

Headers Supporting Roof and Ceiling Only (50 ksi steel) a, b Reserved.

TABLE R603.6(15)

BACK-TO-BACK HEADER SPANS

Headers Supporting Roof and Ceiling Only (33 ksi steel)a, b  Reserved.

TABLE R603.6(16)

BACK-TO-BACK HEADER SPANS

Headers Supporting Roof and Ceiling Only (50 ksi steel) a, b  Reserved.

TABLE R603.6(17)

BACK-TO-BACK HEADER SPANS

Headers Supporting One Floor, Roof and Ceiling (33 ksi steel) a, b  Reserved.

TABLE R603.6(18)

BACK-TO-BACK HEADER SPANS

Headers Supporting One Floor, Roof and Ceiling (50 ksi steel) a, b  Reserved.

TABLE R603.6(19)

BACK-TO-BACK HEADER SPANS

Headers Supporting One Floor, Roof and Ceiling (33 ksi steel) a, b  Reserved.

TABLE R603.6(20)

BACK-TO-BACK HEADER SPANS

Headers Supporting One Floor, Roof and Ceiling (50 ksi steel) a, b  Reserved.

TABLE R603.6(21)

BACK-TO-BACK HEADER SPANS

Headers Supporting Two Floors, Roof and Ceiling (33 ksi steel) a, b  Reserved.

TABLE R603.6(22)

BACK-TO-BACK HEADER SPANS

Headers Supporting Two Floors, Roof and Ceiling (50 ksi steel) a, b  Reserved.

TABLE R603.6(23)

BACK-TO-BACK HEADER SPANS

Headers Supporting Two Floors, Roof and ceiling (50 ksi steel) a, b  Reserved.

TABLE R603.6(24)

BACK-TO-BACK HEADER SPANS

Headers Supporting Two Floors, Roof and Ceiling (50 ksi steel) a, b  Reserved.

TABLE R603.7(2)

HEADER TO KING STUD CONNECTION REQUIREMENTSa, b, c, d

Use table from the 2007 FBC. Residential “Table R603.6(10).

For SI: 1 inch = 25.4 mm, 1 foot = 304.8 mm, 1 mile per hour = 0.447 m/s, 1 pound = 4.448 N.

a. All screw sizes shown are minimum.

b. For headers located on the first floor of a two-story building or the first or second floor of a three-story building, the total number of screws is permitted to be reduced by 2 screws, but the total number of screws shall be no less than 4.

c. For roof slopes of 6:12 or greater, the required number of screws may be reduced by half, but the total number of screws shall be no less than four.

d. Screws can be replaced by an uplift connector which has a capacity of the number of screws multiplied by 164 pounds (e.g., 12-No. 8 screws can be replaced by an uplift connector whose capacity exceeds 12 ﾗ164 pounds = 1,968 pounds).

R603.9.5 Structural sheathing for stone and masonry veneer.   Reserved.

Section R606.2 Thickness of masonry. Change to read as shown:

R606.2 Thickness of masonry. The minimum nominal thickness of exterior concrete masonry walls shall be 8 inches (203 mm) or shall be designed in accordance with Section R606.1.

R606.2.1 Minimum thickness. Reserved.

R606.2.2 Rubble stone masonry wall. Reserved.

R606.2.3 Change in thickness.  [same as IRC]

R606.2.4 [was FL R606.2.2] Parapet walls. Unreinforced solid masonry parapet walls shall not be less than 8 inches (203 mm) thick and their height shall not exceed four times their thickness. Unreinforced hollow unit masonry parapet walls shall be not less than 8 inches (203 mm) thick, and their height shall not exceed three times their thickness. Masonry parapets shall be reinforced in accordance with ACI 530/ASCE 5/TMS 402. Masonry parapet walls in areas subject to wind loads of 30 pounds per square foot (1.44 kPa) located in Seismic Design Category D0, D1 orD2, or on townhouses in Seismic Design Category C shall be reinforced in accordance with Section R606.12.

R606.3 No change

R606.4 [was FL R606.12] Support conditions.  [same as IRC]

R606.5  Allowable stresses. Change to read as shown:

R606.5 [was FL R606.4] Allowable stresses. Concrete masonry units shall be hollow or solid unit masonry in accordance with ASTMC 90 and shall have a minimum net area compressive strength of 1900 psi in compliance with ASTM C90. Mortal shall comply with Section R607.1. In determining the stresses in masonry, the effects of all loads and conditions of loading and the influence of all forces affecting the design and strength of the several parts shall be taken into account.

R606.5.1 [was FL R606.4.1] Combined units. [same as IRC]

TABLE R606.5 Allowable Compressive Stresses for Empirical Design of Masonry. Reserved.

R606.6 Piers. Reserved.

R606.6.1 [was FL R606.5] Pier cap. [same as IRC]

R606.7 [was FL R606.6] Chases. [same as IRC]

R606.8 Stack bond. Change to read as shown:

R606.8 [was FL R606.7] Bond. Masonry walls shall be running bond or stack bond construction.

R606.8.1 Joint reinforcement stack bond. When masonry units are laid in stack bond, horizontal joint reinforcement shall be placed in bed joints at not more than 16 inches (406 mm) on center. Horizontal joint reinforcement shall be a minimum of  9-gage and shall be in addition to required vertical reinforcement. Joint reinforcement shall be embedded in accordance with Section R606.9.6.

Section R606.9Lateral support.  Change to read as shown.

R606.9 Reinforcement. Reinforcing steel shall be a minimum of Grade 60 or Grade 40 No. 5 or No. 4 bars and shall be identified in an approved manner.

R606.9.1 Bundling. Bundling shall be permitted when two bars are required at the same location in a wall or in a bond beam.

R606.9.2 Splicing. Splices shall be lap splices. Noncontact lap splices shall be permitted, provided reinforcing bars are not spaced farther apart than 5 inches (127 mm). Splice lengths shall be in accordance with Table R606.9.2 and shall be a minimum of 25 inches (635 mm for No. 5 bars and 20 inches (508 mm) for No. 4 bars.

Table R606.9.2 Lap Splice Lengths.  Add to read as shown.

| TABLE R606.9.2 |  |
| --- | --- |
| LAP SPLICE LENGTHS |  |
| Bar Size (No.) | Lap Length (in.) |
| 3 | 15 |
| 4 | 20 |
| 5 | 25 |
| 6 | 34 |
| 7 | 42 |

R606.9.3 Bending. Reinforcement shall be bent in the shop or in the field. All reinforcement shall be bent cold. The diameter of the bend, measured on the inside of the bar, shall not be less than six-bar diameters. Reinforcement partially embedded in concrete shall not be field bent.

Exception: Where bending is necessary to align dowel bars with a vertical cell, bars partially embedded in concrete shall be permitted to be bent at a slope of not more than 1 inch (25 mm) of horizontal displacement to 6 inches (152 mm) of vertical bar length.

R606.9.4 Clearance from masonry. Reinforcing bars embedded in grouted masonry cells shall have a minimum clear distance between reinforcing bars and any face of a cell of 1/4-inch (6.4 mm) for fine grout or 1/2-inch (12.7 mm) for coarse grout.

R606.9.5 Cover for reinforcing steel. Reinforcing bars used in masonry walls shall have a masonry cover, including grout, of not less than 2 inches (51 mm) for masonry units with face exposed to earth or weather and 11/2 inch (38 mm) for masonry units not exposed to earth or weather.

R606.9.6 Joint reinforcement embedment. Longitudinal wires of joint reinforcement shall be fully embedded in mortar or grout with a minimum cover of 5/8-inch (15.9 mm) when exposed to earth or weather and 1/2-inch (12.7 mm) when not exposed to earth or weather.

R606.9.7 Cleanout openings. Cleanout openings shall be provided for cells containing spliced reinforcement when the grout pour exceeds 5 feet (1524 mm) in height. Where cleanout openings are required, an opening shall be provided in the bottom course of the masonry cell to be filled. Cleanout openings shall have a minimum opening dimension of 3 inches (76 mm).

R606.9.8 Termination. All vertical wall reinforcement shall be terminated by hooking into a bond beam or footing with a standard hook. Standard hooks shall be formed by bending the vertical wall reinforcement in accordance with Section R606.9.3 or shall be a prefabricated standard hook. Splices to standard hooks shall be lap splices with the minimum extension length beyond the bend for standard hooks of 10 inches (254 mm) for No. 5 bars and 8 inches (203 mm) for No. 4 bars. Hooks at bond beams shall extend to the uppermost horizontal reinforcement of the bond beam and shall be embedded a minimum of 6 inches (152 mm) into the bond beam as detailed in Figures R606.9a and R606.9b. Where multiple bars are required, a single standard hook shall terminate into the bond beam or footing. In narrow footings where the width is insufficient to accommodate a standard 90-degree (1.57 rad) hook and provide the concrete cover required by Section 1907.7.1 of the Florida Building Code, Building, the hook shall be rotated in the horizontal direction until the required concrete cover is achieved.

R606.9.9 Continuity multistory construction. Vertical wall reinforcement in multistory construction shall extend through bond beams and shall be continuous with the vertical wall reinforcement of the wall above or be offset in accordance with Section R606.9.9.1 and Figure R606.9.9B.

Exception: Where more than one bar in the same cell is required for vertical wall reinforcement, only one bar shall be required to be continuous between stories.

R606.9.9.1 Offset reinforcement. Vertical reinforcement shall be permitted to be offset between floor levels. Reinforcement for the lower story shall be anchored into the upper floor level bond beam, and reinforcement for the upper story shall be anchored into the bond beams above and below in accordance with Section R606.9.8 and Figures R606.9.9A and R606.9.9B.

R606.10 [was FLR606.8] Lintels  [same as IRC]

R606.11Anchorage.  Reserved.

FIGURE R606.11(1)

ANCHORAGE REQUIREMENTS FOR MASONRY WALLS LOCATED IN SEISMIC

DESIGN CATEGORY A, B OR C AND WHERE WIND LOADS ARE LESS THAN 30 PSF

Reserved

FIGURE R606.11(2)

REQUIREMENTS FOR REINFORCED GROUTED MASONRY CONSTRUCTION IN SEISMIC DESIGN CATEGORY C

Reserved.

FIGURE R606.11(3)

REQUIREMENTS FOR REINFORCED MASONRY CONSTRUCTION IN SEISMIC DESIGN CATEGORY D0, D1, OR D2

Reserved.

R606.12 Seismic requirements.  Reserved.

R606.12.1 General. [All] Reserved.

R606.12.2 Seismic Design Category C. [All]  Reserved.

R606.12.3 Seismic Design Category D0 or D1. [All]  Reserved.

R606.12.4 Seismic Design Category D2. [All]   Reserved.

TABLE R606.12.3.2

MINIMUM DISTRIBUTED WALL REINFORCEMENT FOR BUILDING ASSIGNED TO SEISMIC DESIGN CATEGORY D0 or D1  Reserved.

TABLE R606.12.4.1

MINIMUM REINFORCING FOR STACKED BONDED

MASONRY WALLS IN SEISMIC DESIGN CATEGORY D2  Reserved.

TABLE R606.12.4.2

MINIMUM REINFORCING FOR STACKED BONDED MASONRY

WALLS IN SEISMIC DESIGN CATEGORY D2  Reserved.

Section R606.14 Beam supports. [same as IRC]

R606.14.1 Joist bearing. Change to read as shown:

R606.14.1 [was FL R606.11.1] Joist bearing. Except where supported on a 1-inch by 4-inch (25.4 mm by 102 mm) ribbon strip and nailed to the adjoining stud and as provided in Section R606.11, the ends of each joist shall not have less than 11/2 inches (38 mm) of bearing on wood or metal, or less than 3 inches (76 mm) on masonry.

R606.15 [was FL R606.10] Metal accessories. [same as IRC]

R606.15.1 [was FL R606.10.1] Corrosion protection. [same as IRC]

Section R606.16 Add to read as shown.

R606.16 [was FL R606.13] Masonry opening tolerances. Masonry rough openings may vary in the cross section dimension or elevation dimension specified on the approved plans from - ¼ inches (6.4 mm) to + ½ inches (12.7 mm). For exterior window and door installation provisions see Sections R612.11 and R612.12.

R607.1.2 Masonry in Seismic Design Categories A, B and C.  Reserved.

R607.1.3 Masonry in SeismicDesignCategoriesD0,D1 and D2.  Reserved.

Section R609.1. General.  Change to read as shown.

R609.1 General. Grouted hollow unit masonry is a form of construction in which certain cells of hollow units are continuously filled with grout.

R609.1.1 Grout. Grout shall consist of cementitious material and aggregate in accordance with ASTM C 476 and the proportion specifications of Table R609. 1.1. Type M or Type S mortar to which sufficient water has been added to produce pouring consistency can be used as grout when it has been tested in accordance with ASTM C 1019 and is shown to meet the minimum required specified strength of  2500 psi or the specified f\m if greater than 2500 psi.  Additionally, a slump test must be done to each batch to assure that it meets the required 8 to 11 inch slump.

R609.1.2 Grout lift height. Where the following conditions are met, place grout in lifts not exceeding 12.67 feet (3.86 m).

1. The masonry has cured for at least 4 hours.

2. The grout slump is maintained between 10 and 11 inches (254 and 279 mm).

3. No intermediate reinforced bond beams are placed between the top and the bottom of the pour height.

Otherwise, place grout in lifts not exceeding 5 feet (1524 mm). If grouting is stopped for one hour or longer, the horizontal construction joints shall be formed by stopping all tiers at the same elevation and with the grout 1 inch (25.4 mm) below the top.

Table R609.1.2 Grout Space Dimensions and Pour Heights. Reserved.

R609.1.3 Grout space (cleaning). [same as IRC]

R609.1.4 Grout placement. All cells containing reinforcement or anchor bolts shall be grouted solid. Grout shall be a plastic mix suitable for pumping without segregation of the constituents and shall be mixed thoroughly. Grout shall have a maximum coarse aggregate size of 3/8 inch (9.5 mm) and shall be placed at an 8- to 11-inch (203 to 279 mm) slump and shall have a minimum specified compressive strength of 2000 psi at 28 days when tested in an approved manner or shall be in accordance with ASTM C 476. Grout shall be placed by pumping or by an approved alternate method and shall be placed before any initial set occurs and in no case more than 11/2 hours after water has been added. Grouting shall be done in a continuous pour, in lifts in accordance with Section R609.1.2. Grout shall be consolidated at the time of placement in accordance with the following:

1. Consolidate grout pours 12 inches (305 mm) or less in height by mechanical vibration or by puddling.

2. Consolidate pours exceeding 12 inches (305 mm) in height by mechanical vibration, and reconsolidate by mechanical vibration after initial water loss and settlement has occurred.

R609.1.4.1 Grout pumped through aluminum pipes. [same as IRC]

TABLE R609.1.1 GROUT PROPORTIONS BY VOLUME FOR MASONRY CONSTRUCTION [same as IRC]

TABLE R609.1.2 GROUT SPACE DIMENSIONS AND POUR HEIGHTS. Reserved.

R609.1.5 Cleanouts. Cleanouts shall be provided at the bottom course at each pour of grout where such pour exceeds 5 feet (1524 mm) in height and where required by the building official. Cleanouts shall be provided with an opening of sufficient size to permit removal of debris. The minimum opening dimension shall be 3 inches (76.2 mm). The cleanouts shall be sealed before grouting and after inspection.

R609.1.5.1 Grouted multiple-wythe masonry. [same as IRC]

R609.1.5.2 Grouted hollow unit masonry. Reserved.

R609.2 Grouted multiple-wythe masonry. Change to read as shown:

R609.2 Bond beams. A reinforced bond beam shall be provided in masonry walls at the top of the wall and at each floor level of each exterior wall. Masonry walls not extending to the roof line shall have a bond beam at the top of the wall.

Exceptions:

1.	A bond beam is not required at the floor level for slab-on-ground floors.

2.	Gable end walls shall be in conformance with Section R609.4.

R609.2.1 Bond beam types. Bond beams shall be one of the following:

1.	8" thick x 8" high masonry

8" thick x 12" high masonry

8" thick x 16" high masonry

8" thick by 24" high masonry

8" thick x 32" high masonry

2.	Precast units certified by the manufacturer for the uplift loads as set forth in Table R802.2.9.1. Precast units shall be installed in accordance with the manufacturer’s specifications and approved by the building official.

R609.2.2 Bond beam reinforcement. The minimum reinforcement for bond beam roof diaphragm chord tension reinforcement steel shall be as set forth in Tables R609.2.2A-1 through R609.2.2A-4 for the appropriate grade of steel and exposure category. The minimum reinforcement for bond beam uplift resisting reinforcement steel shall be as set forth in Tables R609.2.2B-1 through R609.2.2B-8 for the loads set forth in Table R802.2.9.1. The total minimum area of bond beam reinforcement shall be the sum of the required area of the diaphragm chord tension steel and the required area of bond beam uplift steel. Bond beam area shall be converted to bar size in accordance with Table R609.2.2C.

R609.2.3 Location of reinforcement. Reinforcement shall be located in the top of bond beams and in the top and bottom of bond beams also serving as lintels.

R609.2.4 Corner continuity. Reinforcement in bond beams shall be continuous around corners as detailed in Figure R609.2.4.

Exception: In bond beams requiring two reinforcing bars, one bar shall be continuous around corners.

R609.2.5 Change in height. Changes in bond beam height shall be permitted as detailed in Figure R609.2.5.

R609.2.6 Precast units reinforcement. Precast bond beams shall properly receive and retain all vertical wall reinforcement. Precast bond beams shall contain the minimum amount of continuous reinforcement set forth in Sections R609.2.2 and R609.6 as applicable and shall be reinforced at joints to act as drag struts and diaphragm chords.

TABLE R609.2.2C

BOND BEAM AREA OF STEEL PROVIDED IN2/FT

| Number of Bars | BAR SIZE |  |  |
| --- | --- | --- | --- |
|  | No. 4 | No. 5 | No. 6 |
| 1 | 0.20 | 0.31 | 0.44 |
| 2 | 0.40 | 0.62 | 0.88 |

Add Figures R609.2.4 and R609.2.5 as shown in the FBC-R 2007.

FIGURE R609.2.4

CORNER CONTINUITY OF BOND BEAM AND WALL REINFORCEMENT

FIGURE R609.2.5

CHANGES IN BOND BEAM HEIGHT

R609.3 Reinforced grouted multiple-wythe masonry.  Replace to read as shown:

R609.3 Vertical reinforcement. Vertical reinforcement shall be provided in conformance with Sections R609.3.1 through R609.3.6.

R609.3.1 One reinforcement bar shall be provided in each corner, including interior corners and corners created by changes in wall direction or offsetting of walls.

R609.3.2 Openings. A minimum of one bar of the size used for vertical wall reinforcement shall be provided on each side of openings wider than 6 feet (1829 mm). If more vertical reinforcement is interrupted by an opening than is provided beside the opening (total in the first and second cells adjacent to the opening), one-half of the equivalent area of reinforcement interrupted by the opening shall be placed on each side of the opening. This reinforcement shall be placed within the first and/or second cells beside the opening.

R609.3.2.1 Girders. At least one reinforcement bar shall be provided where girders or girder trusses bear on masonry walls.

R609.3.3 Spacing. Vertical reinforcement shall be provided as set forth in Tables R609.3.3.A-1 through R609.3.3A-4 and Tables R609.3.3.B-1, through R609.3.3B-4 as applicable.

R609.3.4 Precast bond beams. Vertical reinforcement used in conjunction with precast bond beams shall be spaced the same as for masonry bond beams. Reinforcement shall terminate in the precast beam as set forth in Section R606.9.8.

R609.3.5 Duplication. Reinforcing steel requirements shall not be additive. A single bar shall be permitted to satisfy multiple requirements.

R609.3.6 Termination. Vertical reinforcement shall terminate in footings and bond beams as set forth in Section R606.9.8.

R609.4 Reinforced hollow unit masonry. Replace to read as shown:

R609.4 Masonry gables. Gable end walls of concrete or masonry shall be constructed full height to the roof line.

Exception: Gable end trusses or wood framed gable end walls in conformance with Tables R609.4A and R609.4B and Figure R609.4. Wood gable stud wall connectors shall be capable of resisting the vertical and horizontal loads of Table R609.4B as well as the uplift load stipulated at Figure R609.4. Where masonry gable end walls do not go to the roof, a bond beam complying with Section R609.2 shall be provided at the top of the masonry.

R609.4.1 Rake beam. Where concrete or masonry is carried full height to the roof line, a cast-in-place rake beam as detailed in Figure R609.4.1 shall be provided. The minimum thickness of the rake beam from top of masonry shall be 4 inches (102 mm). One No. 5 continuous reinforcing bar shall be placed in the rake beam along the roof line.

R609.4.2 Vertical reinforcement. Vertical reinforcement shall be provided at the maximum spacing as set forth in Tables R609.3.3B-1 through R609.3.3.B-4 as applicable.

R609.4.3 Termination. Required vertical reinforcement shall terminate at the rake beam in accordance with Section R606.9.8.

R609.4.4 Nailer. A minimum 2´4 nailer for connecting roof sheathing shall be bolted to the top of the wall with a minimum of 1/2 inch (12.7 mm) anchor bolts spaced as set forth in Table R609.4.4. The nailer shall be permitted to be bolted to the inside or outside of the wall.

R609.4.5 Gable overhang. Gable overhangs up to 2 feet (610 mm) in width complying with Figure R609.4.5 shall be permitted.

R609.5  Add to read as shown:

R609.5 Exterior shearwalls. Each exterior wall shall have the required length of effective shearwall to resist horizontal movement or forces at the ends of diaphragms in conformance with this section.

R609.5.1 Shearwall lengths. The required shearwall segment length shall be as set forth in Tables R609.5.1A through R609.5.1R as applicable.

R609.5.2 Multistory shearwalls. Shearwall segments in an upper story shall be located directly over and within the length of shearwall segments in the story below. Reinforcement at the ends of shearwall segments shall be continuous from the bond beam of the upper story through the story below.

R609.5.3 The connector load for total shear at the top story wall shall be determined in accordance with Table R609.5.3A and Figure R609.5.3. Transverse connector loads shall be in accordance with Table R609.5.3B and Figure R609.5.3.

R609.5.4 Endwall roof shear loads shall be in accordance with Table R609.5.4.

Add Tables R609.2.2A-1, R609.2.2A-2, R609.2.2A-3, R609.2.2A-4, R609.2.2B-1, R609.2.2B-2, R609.2.2B-3, R609.2.2B-4, R609.2.2B-5, R609.2.2B-6, R609.2.2B-7, R609.2.2B-8, R609.3.3A-1, R609.3.3A-2, R609.3.3A-3, R609.3.3A-4, R609.3.3B-1, R609.3.3B-2, R609.3.3B-3, R609.3.3B-4, R609.4A, R609.4B, R609.5.1A, R609.5.1B, R609.5.1C, R609.5.1D, R609.5.1E, R609.5.1F, R609.5.1G, R609.5.1H, R609.5.1I, R609.5.1J, R609.5.1K, R609.5.1L, R609.5.1M, R609.5.1N, R609.5.1O, R609.5.1P, R609.5.1Q, R609.5.1R from the 2007 FBC-Residential as amended by the 2009 Supplement to the 2007 FBC-R.

TABLE R609.3.3A-4 GRADE 40

SINGLE STORY AND TOP STORY WALLS PARALLEL TO RIDGE VERTICAL

REINFORCEMENT SPACING No. 4 BARS (1/2”)

|  | Exposure | B | B | B | C | C | C |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Building Width |  |  |  |  |  |
| Wind Speed | Wall Height | 24 | 32 | 40 | 24 | 32 | 40 |
| 100 | 8.00 | 8.78 | 8.04 | 7.42 | 5.82 | 5.31 | 4.88 |
|  | 8.67 | 7.77 | 7.19 | 6.69 | 5.19 | 4.78 | 4.43 |
|  | 9.33 | 6.83 | 6.46 | 6.05 | 4.66 | 4.32 | 4.03 |
|  | 10.00 | 6.04 | 5.81 | 5.48 | 4.18 | 3.91 | 3.67 |
|  | Exposure | B | B | B | C | C | C |
|  |  | Building Width |  |  |  |  |  |
| Wind Speed | Wall Height | 24 | 32 | 40 | 24 | 32 | 40 |
| 110 | 8.00 | 6.94 | 6.34 | 5.84 | 4.67 | 4.25 | 3.90 |
|  | 8.67 | 6.42 | 6.42 | 6.42 | 4.56 | 4.56 | 4.56 |
|  | 9.33 | 5.63 | 5.63 | 5.63 | 4.00 | 4.00 | 4.00 |
|  | 10.00 | 4.98 | 4.98 | 4.98 | 3.53 | 3.53 | 3.53 |
|  | Exposure | B | B | B | C | C | C |
|  |  | Building Width |  |  |  |  |  |
| Wind Speed | Wall Height | 24 | 32 | 40 | 24 | 32 | 40 |
| 120 | 8.00 | 5.64 | 5.15 | 4.73 | 3.84 | 3.49 | 3.20 |
|  | 8.67 | 5.38 | 5.38 | 5.38 | 3.82 | 3.82 | 3.82 |
|  | 9.33 | 4.72 | 4.72 | 4.72 | 3.35 | 3.35 | 3.35 |
|  | 10.00 | 4.17 | 4.17 | 4.17 | 2.95 | 2.95 | 2.95 |
|  | Exposure | B | B | B | C | C | C |
|  |  | Building Width |  |  |  |  |  |
| Wind Speed | Wall Height | 24 | 32 | 40 | 24 | 32 | 40 |
| 130 | 8.00 | 4.69 | 4.27 | 3.92 | 3.21 | 2.92 | 2.67 |
|  | 8.67 | 4.19 | 3.86 | 3.57 | 2.88 | 2.64 | 2.44 |
|  | 9.33 | 3.77 | 3.49 | 3.25 | 2.60 | 2.40 | 2.23 |
|  | 10.00 | 3.39 | 3.17 | 2.97 | 2.34 | 2.18 | 2.04 |
|  | Exposure | B | B | B | C | C | C |
|  |  | Building Width |  |  |  |  |  |
| Wind Speed | Wall Height | 24 | 32 | 40 | 24 | 32 | 40 |
| 140 | 8.00 | 3.97 |  |  |  |  |  |
|  | 8.67 |  |  |  |  |  | 3.11 |
|  | 9.33 | 3.29 | 2.96 | 2.75 | 2.21 | 2.04 | 1.90 |
|  | 10.00 | 2.88 | 2.69 | 2.52 | 4.93 | 1.86 | 1.74 |
|  | Exposure | B | B | B | C | C | C |
|  |  | Building Width |  |  |  |  |  |
| Wind Speed | Wall Height | 24 | 32 | 40 | 24 | 32 | 40 |
| 150 | 8.00 | 3.40 | 3.00 | 2.93 | 2.35 | 2.13 | 1.95 |
|  | 8.67 |  |  | 2.58 | 2.11 |  | 1.78 |
|  | 9.33 | 2.75 | 2.54 | 2.36 | 1.90 | 1.76 | 1.63 |
|  | 10.00 | 2.48 | 2.37 | 2.16 | 1.72 | 1.60 | 1.50 |

[NOTE:  Delete bad copy of table below once numbers are verified.]

Table R609.3.3A-2 Grade 60 Single Story and Top Story Walls Parallel to Ridge Vertical Reinforcement Spacing No. 4 Bars (1/2”) is revised to read as follows:

TABLE R609.3.3A-2 GRADE 60

SINGLE STORY AND TOP STORY WALLS PARALLEL TO RIDGE VERTICAL

REINFORCEMENT SPACING No. 4 BARS (1/2”)

|  | Exposure | B | B | B | C | C | C |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Building Width |  |  |  |  |  |
| Wind Speed | Wall Height | 24 | 32 | 40 | 24 | 32 | 40 |
| 100 | 8.00 | 9.87 | 9.87 | 9.87 | 8.34 | 7.97 | 7.32 |
|  | 8.67 | 9.97 | 9.97 | 9.97 | 7.79 | 7.17 | 6.65 |
|  | 9.33 | 10.06 | 9.69 | 9.08 | 6.98 | 6.48 | 6.05 |
|  | 10.00 | 9.06 | 8.72 | 8.22 | 6.27 | 5.87 | 5.51 |
|  | Exposure | B | B | B | C | C | C |
|  |  | Building Width |  |  |  |  |  |
| Wind Speed | Wall Height | 24 | 32 | 40 | 24 | 32 | 40 |
| 110 | 8.00 | 8.97 | 8.97 | 8.76 | 7.01 | 6.38 | 5.85 |
|  | 8.67 | 9.06 | 9.06 | 9.06 | 6.83 | 6.83 | 6.83 |
|  | 9.33 | 8.45 | 8.45 | 8.45 | 5.99 | 5.99 | 5.99 |
|  | 10.00 | 7.47 | 7.47 | 7.47 | 5.30 | 5.30 | 5.30 |
|  | Exposure | B | B | B | C | C | C |
|  |  | Building Width |  |  |  |  |  |
| Wind Speed | Wall Height | 24 | 32 | 40 | 24 | 32 | 40 |
| 120 | 8.00 | 8.23 | 7.72 | 7.09 | 5.75 | 5.23 | 4.80 |
|  | 8.67 | 8.07 | 8.07 | 8.07 | 5.72 | 5.72 | 5.72 |
|  | 9.33 | 7.08 | 7.08 | 7.08 | 5.02 | 5.02 | 5.02 |
|  | 10.00 | 6.26 | 6.26 | 6.26 | 4.43 | 4.43 | 4.43 |
|  | Exposure | B | B | B | C | C | C |
|  |  | Building Width |  |  |  |  |  |
| Wind Speed | Wall Height | 24 | 32 | 40 | 24 | 32 | 40 |
| 130 | 8.00 | 7.04 | 6.41 | 5.88 | 4.82 | 4.38 | 4.01 |
|  | 8.67 | 6.29 | 5.78 | 5.35 | 4.32 | 3.96 | 3.66 |
|  | 9.33 | 5.65 | 5.24 | 4.88 | 3.89 | 3.60 | 3.35 |
|  | 10.00 | 5.09 | 4.75 | 4.45 | 3.51 | 3,.27 | 3.06 |
|  | Exposure | B | B | B | C | C | C |
|  |  | Building Width |  |  |  |  |  |
| Wind Speed | Wall Height | 24 | 32 | 40 | 24 | 32 | 40 |
| 140 | 8.00 |  | -- | -- | -- | -- | -- |
|  | 8.67 |  |  |  | 3.65 | 3.37 | 3.11 |
|  | 9.33 | 4.79 | 4. |  |  |  |  |
|  | 10.00 |  |  |  |  |  |  |
|  | Exposure | B | B | B | C | C | C |
|  |  | Building Width |  |  |  |  |  |
| Wind Speed | Wall Height | 24 | 32 | 40 | 24 | 32 | 40 |
| 150 | 8.00 | 5.10 | 4.63 | 4.25 | 3.53 | 3.20 | 2.93 |
|  | 8.67 | 4.57 | 4.20 | 3.07 | 3.17 | 2.90 | 2.00 |
|  | 9.33 | 4.12 | 3.81 | 3.54 | 2.86 | 2.64 | 2.45 |
|  | 10.00 | 3.71 | 3.46 | 3.24 | 2.58 | 2.40 | 2.24 |

[NOTE:  Delete bad copy of table below once numbers are verified.]

Table R609.5.1.A Grade 60, revise text to read as follows:

| TABLE R609.5.1A Grade 60 |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| REQUIRED SHEARWALL LENGTH PARALLEL TO RIDGE NO. 4 REINFORCEMENT1,2,3,5 |  |  |  |  |  |  |  |  |  |  |
|  |  | ROOF ANGLE ≤23° |  |  |  |  |  |  |  |  |
| TOP STORY |  |  |  |  | 1ST STORY OF 2 STORY OR 2ND STORY OF 3 STORY |  |  | 1ST STORY OF 3 STORY |  |  |
| Exp-osure | Wind Speed | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  |
|  |  | 24 | 32 | 40 | 24 | 32 | 40 | 24 | 32 | 40 |
| B | 100 | 1.62 | 2.31 | 3.14 | 3.68 | 4.98 | 6.49 | 5.41 | 7.28 | 9.43 |
|  | 110 | 1.96 | 2.79 | 3.80 | 4.45 | 6.03 | 7.85 | 6.55 | 8.81 | 11.42 |
|  | 120 | 2.33 | 3.32 | 4.52 | 5.30 | 7.17 | 9.34 | 7.79 | 10.48 | 13.58 |
|  | 130 | 2.73 | 3.90 | 5.31 | 6.22 | 8.42 | 10.96 | 9.14 | 12.30 | 15.94 |
|  | 140 | 3.17 | 4.52 | 6.16 | 7.22 | 9.76 | 12.71 | 10.60 | 14.27 | 18.49 |
|  | 150 | 3.64 | 5.19 | 7.07 | 8.28 | 11.21 | 14.59 | 12.17 | 16.38 | 21.23 |
| C | 100 | 1.92 | 2.77 | 3.82 | 4.86 | 6.63 | 8.69 | 7.56 | 10.15 | 13.13 |
|  | 110 | 2.32 | 3.35 | 4.62 | 5.88 | 8.02 | 10.52 | 9.14 | 12.28 | 15.88 |
|  | 120 | 2.76 | 3.99 | 5.50 | 7.00 | 9.54 | 12.52 | 10.88 | 14.61 | 18.90 |
|  | 130 | 3.24 | 4.68 | 6.46 | 8.21 | 11.20 | 14.69 | 12.77 | 17.15 | 22.18 |
|  | 140 | 3.76 | 5.43 | 7.49 | 9.53 | 12.99 | 17.04 | 14.81 | 19.89 | 25.73 |
|  | 150 | 4.32 | 6.23 | 8.59 | 10.94 | 14.91 | 19.56 | 17.00 | 22.83 | 29.53 |
| REQUIRED SHEARWALL LENGTH PARALLEL TO RIDGE NO. 5 REINFORCEMENT1,2,3,6 |  |  |  |  |  |  |  |  |  |  |
|  |  | ROOF ANGLE ≤23° |  |  |  |  |  |  |  |  |
| TOP STORY |  |  |  |  | 1ST STORY OF 2 STORY OR 2ND STORY OF 3 STORY |  |  | 1ST STORY OF 3 STORY |  |  |
| Exp-osure | Wind Speed | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  |
|  |  | 24 | 32 | 40 | 24 | 32 | 40 | 24 | 32 | 40 |
| B | 100 | 1.09 | 1.55 | 2.12 | 2.48 | 3.35 | 4.37 | 3.64 | 4.90 | 6.35 |
|  | 110 | 1.32 | 1.88 | 2.56 | 3.00 | 4.06 | 5.28 | 4.41 | 5.93 | 7.68 |
|  | 120 | 1.57 | 2.23 | 3.05 | 3.57 | 4.83 | 6.29 | 5.24 | 7.06 | 9.14 |
|  | 130 | 1.84 | 2.62 | 3.57 | 4.19 | 5.67 | 7.38 | 6.16 | 8.28 | 10.73 |
|  | 140 | 2.13 | 3.04 | 4.15 | 4.86 | 6.57 | 8.56 | 7.14 | 9.60 | 12.45 |
|  | 150 | 2.45 | 3.49 | 4.76 | 5.58 | 7.54 | 9.82 | 8.19 | 11.02 | 14.29 |
| C | 100 | 1.29 | 1.86 | 2.57 | 3.27 | 4.46 | 5.85 | 5.09 | 6.83 | 8.84 |
|  | 110 | 1.56 | 2.26 | 3.11 | 3.96 | 5.40 | 7.08 | 6.16 | 8.26 | 10.69 |
|  | 120 | 1.86 | 2.68 | 3.70 | 4.71 | 6.42 | 8.43 | 7.33 | 9.84 | 12.72 |
|  | 130 | 2.18 | 3.15 | 4.35 | 5.53 | 7.54 | 9.89 | 8.60 | 11.54 | 14.93 |
|  | 140 | 2.53 | 3.65 | 5.04 | 6.41 | 8.74 | 11.47 | 9.97 | 13.39 | 17.32 |
|  | 150 | 2.91 | 4.19 | 5.79 | 7.36 | 10.04 | 13.17 | 11.45 | 15.37 | 19.88 |
| Notes: |  |  |  |  |  |  |  |  |  |  |

1.	The cumulative shear wall segment length for each side of the building shall be equal to or greater than the tabular shear wall length required.  If the required shear wall segment length provided is not one continuous shear wall segment, the total shear wall length required shall be increased by 0.67 feet (8 inches) for each additional shear wall segment making up the total shear wall length on a side.

2.	The minimum shear wall segment length shall be 2 feet-0 inches.   Values less than 2 feet-0 inches ( are shown only for summation of shear wall segments and for interpolation purposes.  A grouted cell with vertical reinforcement of the size indicated is required at each end of every shear wall segment.

3.    Other than incidental utility

penetrations, shearwall piers and shearwall segments shall not contain openings with a maximum horizontal or vertical dimension of 5 inches for piers and 12 inches for portions of shearwall segments above and below piers. The total area of openings in any one segment of shearwall shall not exceed 144 square inches.

4.	Required shearwall lengths normal (perpendicular) to the ridge are per lineal foot of building length. Multiply tabular values by building length (distance between adjacent shear walls perpendicular to the ridge if interior shear walls are used for total shear wall length required.

5.	Shear wall lengths are based on shear wall segment heights of 80 inches (height from the floor to the top of the highest opening adjacent to the shear segment—corners and openings as permitted by Note 3 of this table are not considered for the purpose of this measurement). For shear segment heights other than 80 inches, multiply tabular length values as follows:

| Segment Height (inches) | Length Multiplier |
| --- | --- |
| 88 | 1.09 |
| 96 | 1.19 |
| 104 | 1.28 |
| 112 | 1.37 |

7

Table R609.5.1B Grade 60, revise text to read as follows:

| TABLE R609.5.1B Grade 60 |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| REQUIRED SHEARWALL LENGTH PARALLEL TO RIDGE NO. 4 REINFORCEMENT1,2,3,5 |  |  |  |  |  |  |  |  |  |  |
|  |  | ROOF ANGLE 30° |  |  |  |  |  |  |  |  |
| TOP STORY |  |  |  |  | 1ST STORY OF 2 STORY OR 2ND STORY OF 3 STORY |  |  | 1ST STORY OF 3 STORY |  |  |
| Exp-osure | Wind Speed | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  |
|  |  | 24 | 32 | 40 | 24 | 32 | 40 | 24 | 32 | 40 |
| B | 100 | 1.66 | 2.45 | 3.40 | 3.55 | 4.92 | 6.49 | 5.18 | 7.13 | 9.36 |
|  | 110 | 2.01 | 2.96 | 4.11 | 4.30 | 5.96 | 7.86 | 6.27 | 8.63 | 11.32 |
|  | 120 | 2.39 | 3.52 | 4.89 | 5.12 | 7.09 | 9.35 | 7.46 | 10.27 | 13.47 |
|  | 130 | 2.81 | 4.13 | 5.74 | 6.00 | 8.32 | 10.97 | 8.76 | 12.05 | 15.81 |
|  | 140 | 3.26 | 4.79 | 6.66 | 6.96 | 9.65 | 12.73 | 10.15 | 13.98 | 18.34 |
|  | 150 | 3.74 | 5.50 | 7.64 | 7.99 | 11.08 | 14.61 | 11.66 | 16.05 | 21.05 |
| C | 100 | 2.00 | 2.99 | 4.21 | 4.73 | 6.62 | 8.82 | 7.22 | 9.92 | 12.97 |
|  | 110 | 2.42 | 3.62 | 5.10 | 5.72 | 8.01 | 10.67 | 8.74 | 12.00 | 15.70 |
|  | 120 | 2.88 | 4.30 | 6.07 | 6.81 | 9.53 | 12.70 | 10.40 | 14.28 | 18.68 |
|  | 130 | 3.37 | 5.05 | 7.12 | 7.99 | 11.19 | 14.90 | 12.20 | 16.76 | 21.92 |
|  | 140 | 3.91 | 5.86 | 8.26 | 9.27 | 12.98 | 17.28 | 14.15 | 19.43 | 25.43 |
|  | 150 | 4.49 | 6.73 | 9.48 | 10.64 | 14.90 | 19.84 | 16.25 | 22.31 | 29.19 |
| REQUIRED SHEARWALL LENGTH PARALLEL TO RIDGE NO. 5 REINFORCEMENT1,2,3,6 |  |  |  |  |  |  |  |  |  |  |
|  |  | ROOF ANGLE 30° |  |  |  |  |  |  |  |  |
| TOP STORY |  |  |  |  | 1ST STORY OF 2 STORY OR 2ND STORY OF 3 STORY |  |  | 1ST STORY OF 3 STORY |  |  |
| Exp-osure | Wind Speed | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  |
|  |  | 24 | 32 | 40 | 24 | 32 | 40 | 24 | 32 | 40 |
| B | 100 | 1.12 | 1.65 | 2.29 | 2.39 | 3.31 | 4.37 | 3.49 | 4.80 | 6.30 |
|  | 110 | 1.35 | 1.99 | 2.77 | 2.89 | 4.01 | 5.29 | 4.22 | 5.81 | 7.62 |
|  | 120 | 1.61 | 2.37 | 3.29 | 3.44 | 4.77 | 6.29 | 5.02 | 6.91 | 9.07 |
|  | 130 | 1.89 | 2.78 | 3.86 | 4.04 | 5.60 | 7.39 | 5.89 | 8.11 | 10.64 |
|  | 140 | 2.19 | 3.23 | 4.48 | 4.69 | 6.50 | 8.57 | 6.84 | 9.41 | 12.34 |
|  | 150 | 2.52 | 3.71 | 5.14 | 5.38 | 7.46 | 9.83 | 7.85 | 10.80 | 14.17 |
| C | 100 | 1.34 | 2.01 | 2.84 | 3.18 | 4.46 | 5.93 | 4.86 | 6.67 | 8.73 |
|  | 110 | 1.63 | 2.44 | 3.43 | 3.85 | 5.39 | 7.18 | 5.88 | 8.08 | 10.57 |
|  | 120 | 1.94 | 2.90 | 4.08 | 4.58 | 6.42 | 8.55 | 7.00 | 9.61 | 12.57 |
|  | 130 | 2.27 | 3.40 | 4.79 | 5.38 | 7.53 | 10.03 | 8.21 | 11.28 | 14.76 |
|  | 140 | 2.63 | 3.94 | 5.56 | 6.24 | 8.74 | 11.63 | 9.53 | 13.08 | 17.12 |
|  | 150 | 3.02 | 4.53 | 6.38 | 7.16 | 10.03 | 13.35 | 10.94 | 15.02 | 19.65 |
| Notes: |  |  |  |  |  |  |  |  |  |  |

1.	The cumulative shear wall segment length for each side of the building shall be equal to or greater than the tabular shear wall length required.  If the required shear wall segment length provided is not one continuous shear wall segment, the total shear wall length required shall be increased by 0.67 feet (8 inches) for each additional shear wall segment making up the total shear wall length on a side.

2.	The minimum shear wall segment length shall be 2 feet-0 inches.   Values less than 2 feet-0 inches are shown only for summation of shear wall segments and for interpolation purposes.  A grouted cell with vertical reinforcement of the size indicated is required at each end of every shear wall segment.

3.    Other than incidental utility penetrations, shearwall piers and shearwall segments shall not contain openings with a maximum horizontal or vertical dimension of 5 inches for piers and 12 inches for portions of shearwall segments above and below piers. The total area of openings in any one segment of shearwall shall not exceed 144 square inches.

4.	Required shearwall lengths normal (perpendicular) to the ridge are per lineal foot of building length. Multiply tabular values by building length (distance between adjacent shear walls perpendicular to the ridge if interior shear walls are used for total shear wall length required.

5.	Shear wall lengths are based on shear wall segment heights of 80 inches (height from the floor to the top of the highest opening adjacent to the shear segment—corners and openings as permitted by Note 3 of this table are not considered for the purpose of this measurement). For shear segment heights other than 80 inches, multiply tabular length values as follows:

| Segment Height (inches) | Length Multiplier |
| --- | --- |
| 88 | 1.09 |
| 96 | 1.19 |
| 104 | 1.28 |
| 112 | 1.37 |

Table R609.5.1C Grade 60, revise text to read as follows:

| TABLE R609.5.1C Grade 60 |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| REQUIRED SHEARWALL LENGTH PARALLEL TO RIDGE NO. 4 REINFORCEMENT1,2,3,5 |  |  |  |  |  |  |  |  |  |  |
|  |  | ROOF ANGLE 45° |  |  |  |  |  |  |  |  |
| TOP STORY |  |  |  |  | 1ST STORY OF 2 STORY OR 2ND STORY OF 3 STORY |  |  | 1ST STORY OF 3 STORY |  |  |
| Exp-osure | Wind Speed | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  |
|  |  | 24 | 32 | 40 | 24 | 32 | 40 | 24 | 32 | 40 |
| B | 100 | 2.11 | 3.24 | 4.64 | 2.11 | 5.72 | 7.73 | 5.77 | 8.17 | 11.00 |
|  | 110 | 2.56 | 3.92 | 5.61 | 4.85 | 6.92 | 9.36 | 6.98 | 9.89 | 13.31 |
|  | 120 | 3.05 | 4.67 | 6.68 | 5.77 | 8.23 | 11.13 | 8.31 | 11.77 | 15.85 |
|  | 130 | 3.57 | 5.48 | 7.84 | 6.77 | 9.66 | 13.07 | 9.75 | 13.81 | 18.60 |
|  | 140 | 4.15 | 6.35 | 9.09 | 7.85 | 11.20 | 15.16 | 11.31 | 16.02 | 21.57 |
|  | 150 | 4.76 | 7.29 | 10.43 | 9.01 | 12.86 | 17.40 | 12.98 | 18.39 | 24.76 |
| C | 100 | 2.63 | 4.13 | 6.03 | 5.45 | 7.90 | 10.84 | 7.22 | 9.92 | 12.97 |
|  | 110 | 3.18 | 4.99 | 7.30 | 6.60 | 9.56 | 13.12 | 8.74 | 12.00 | 15.70 |
|  | 120 | 3.79 | 5.94 | 8.68 | 7.85 | 11.38 | 15.61 | 10.40 | 14.28 | 18.68 |
|  | 130 | 4.45 | 6.97 | 10.19 | 9.21 | 13.35 | 18.32 | 12.20 | 16.76 | 21.92 |
|  | 140 | 5.16 | 8.09 | 11.82 | 10.68 | 15.48 | 21.25 | 14.15 | 19.43 | 25.43 |
|  | 150 | 5.92 | 9.28 | 13.57 | 12.26 | 17.77 | 24.39 | 16.25 | 22.31 | 29.19 |
| REQUIRED SHEARWALL LENGTH PARALLEL TO RIDGE NO. 5 REINFORCEMENT1,2,3,6 |  |  |  |  |  |  |  |  |  |  |
|  |  | ROOF ANGLE 45° |  |  |  |  |  |  |  |  |
| TOP STORY |  |  |  |  | 1ST STORY OF 2 STORY OR 2ND STORY OF 3 STORY |  |  | 1ST STORY OF 3 STORY |  |  |
| Exp-osure | Wind Speed | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  |
|  |  | 24 | 32 | 40 | 24 | 32 | 40 | 24 | 32 | 40 |
| B | 100 | 1.42 | 2.18 | 3.12 | 2.70 | 3.85 | 5.21 | 3.88 | 5.50 | 7.41 |
|  | 110 | 1.72 | 2.64 | 3.78 | 3.26 | 4.66 | 6.30 | 4.70 | 6.66 | 8.96 |
|  | 120 | 2.05 | 3.14 | 4.49 | 3.88 | 5.54 | 7.50 | 5.59 | 7.92 | 10.67 |
|  | 130 | 2.41 | 3.69 | 5.27 | 4.56 | 6.50 | 8.80 | 6.56 | 9.30 | 12.52 |
|  | 140 | 2.79 | 4.27 | 6.12 | 5.29 | 7.54 | 10.20 | 7.61 | 10.78 | 14.52 |
|  | 150 | 3.20 | 4.91 | 7.02 | 6.07 | 8.66 | 11.71 | 8.74 | 12.38 | 16.67 |
| C | 100 | 1.77 | 2.78 | 4.06 | 3.67 | 5.32 | 7.30 | 5.38 | 7.59 | 10.18 |
|  | 110 | 2.14 | 3.36 | 4.91 | 4.44 | 6.43 | 8.83 | 6.51 | 9.19 | 12.32 |
|  | 120 | 2.55 | 4.00 | 5.85 | 5.28 | 7.66 | 10.51 | 7.75 | 10.93 | 14.66 |
|  | 130 | 2.99 | 4.69 | 6.86 | 6.20 | 8.99 | 12.33 | 9.09 | 12.83 | 17.21 |
|  | 140 | 3.47 | 5.44 | 7.96 | 7.19 | 10.42 | 14.30 | 10.55 | 14.88 | 19.96 |
|  | 150 | 3.98 | 6.25 | 9.13 | 8.26 | 11.96 | 16.42 | 12.11 | 17.09 | 22.91 |
| Notes: |  |  |  |  |  |  |  |  |  |  |

1.	The cumulative shear wall segment length for each side of the building shall be equal to or greater than the tabular shear wall length required.  If the required shear wall segment length provided is not one continuous shear wall segment, the total shear wall length required shall be increased by 0.67 feet (8 inches) for each additional shear wall segment making up the total shear wall length on a side.

2.	The minimum shear wall segment length shall be 2 feet-0 inches.   Values less than 2 feet-0 inches are shown only for summation of shear wall segments and for interpolation purposes.  A grouted cell with vertical reinforcement of the size indicated is required at each end of every shear wall segment.

3.    Other than incidental utility penetrations, shearwall piers and shearwall segments shall not contain openings with a maximum horizontal or vertical dimension of 5 inches for piers and 12 inches for portions of shearwall segments above and below piers. The total area of openings in any one segment of shearwall shall not exceed 144 square inches.

4.	Required shearwall lengths normal (perpendicular) to the ridge are per lineal foot of building length. Multiply tabular values by building length (distance between adjacent shear walls perpendicular to the ridge if interior shear walls are used for total shear wall length required.

5.	Shear wall lengths are based on shear wall segment heights of 80 inches (height from the floor to the top of the highest opening adjacent to the shear segment—corners and openings as permitted by Note 3 of this table are not considered for the purpose of this measurement). For shear segment heights other than 80 inches, multiply tabular length values as follows:

| Segment Height (inches) | Length Multiplier |
| --- | --- |
| 88 | 1.09 |
| 96 | 1.19 |
| 104 | 1.28 |
| 112 | 1.37 |

Table R609.5.1D Grade 60, revise text to read as follows:

| TABLE R609.5.1D Grade 60 |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| REQUIRED SHEARWALL LENGTH PERPENDICULAR TO RIDGE - NO. 4 REINFORCEMENT |  |  |  |  |  |  |  |  |  |  |
| PER FOOT OF BUILDING LENGTH1,2,3,4,5 |  |  |  |  |  |  |  |  |  |  |
| ROOF ANGLE 23° |  |  |  |  |  |  |  |  |  |  |
| TOP STORY |  |  |  |  | 1ST STORY OF 2 STORY OR 2ND STORY OF 3 STORY |  |  | 1ST STORY OF 3 STORY |  |  |
| Exp-osure | Wind Speed | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  |
|  |  | 24 | 32 | 40 | 24 | 32 | 40 | 24 | 32 | 40 |
| B | 100 | 0.054 | 0.053 | 0.053 | 0.142 | 0.142 | 0.141 | 0.231 | 0.231 | 0.230 |
|  | 110 | 0.065 | 0.065 | 0.064 | 0.172 | 0.172 | 0.171 | 0.279 | 0.279 | 0.278 |
|  | 120 | 0.077 | 0.077 | 0.076 | 0.205 | 0.204 | 0.204 | 0.333 | 0.332 | 0.331 |
|  | 130 | 0.091 | 0.090 | 0.089 | 0.240 | 0.240 | 0.239 | 0.390 | 0.390 | 0.389 |
|  | 140 | 0.105 | 0.104 | 0.103 | 0.279 | 0.278 | 0.277 | 0.453 | 0.452 | 0.451 |
|  | 150 | 0.121 | 0.120 | 0.119 | 0.320 | 0.319 | 0.318 | 0.520 | 0.519 | 0.518 |
| C | 100 | 0.075 | 0.075 | 0.074 | 0.199 | 0.199 | 0.198 | 0.324 | 0.323 | 0.322 |
|  | 110 | 0.091 | 0.090 | 0.089 | 0.241 | 0.241 | 0.240 | 0.392 | 0.391 | 0.390 |
|  | 120 | 0.108 | 0.108 | 0.106 | 0.287 | 0.287 | 0.285 | 0.466 | 0.466 | 0.464 |
|  | 130 | 0.127 | 0.126 | 0.125 | 0.337 | 0.336 | 0.335 | 0.547 | 0.546 | 0.545 |
|  | 140 | 0.147 | 0.147 | 0.145 | 0.391 | 0.390 | 0.388 | 0.635 | 0.634 | 0.632 |
|  | 150 | 0.169 | 0.168 | 0.166 | 0.449 | 0.448 | 0.446 | 0.729 | 0.728 | 0.726 |
| REQUIRED SHEARWALL LENGTH PERPENDICULAR TO RIDGE - NO. 5 REINFORCEMENT |  |  |  |  |  |  |  |  |  |  |
| PER FOOT OF BUILDING LENGTH1,2,3,4,6 |  |  |  |  |  |  |  |  |  |  |
| ROOF ANGLE 23° |  |  |  |  |  |  |  |  |  |  |
| TOP STORY |  |  |  |  | 1ST STORY OF 2 STORY OR 2ND STORY OF 3 STORY |  |  | 1ST STORY OF 3 STORY |  |  |
| Exp-osure | Wind Speed | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  |
|  |  | 24 | 32 | 40 | 24 | 32 | 40 | 24 | 32 | 40 |
| B | 100 | 0.036 | 0.036 | 0.035 | 0.096 | 0.096 | 0.095 | 0.155 | 0.155 | 0.155 |
|  | 110 | 0.044 | 0.043 | 0.043 | 0.116 | 0.116 | 0.115 | 0.188 | 0.188 | 0.187 |
|  | 120 | 0.052 | 0.052 | 0.051 | 0.138 | 0.138 | 0.137 | 0.224 | 0.224 | 0.223 |
|  | 130 | 0.061 | 0.061 | 0.060 | 0.162 | 0.162 | 0.161 | 0.263 | 0.262 | 0.262 |
|  | 140 | 0.071 | 0.070 | 0.070 | 0.188 | 0.187 | 0.186 | 0.305 | 0.304 | 0.303 |
|  | 150 | 0.081 | 0.081 | 0.080 | 0.215 | 0.215 | 0.214 | 0.350 | 0.349 | 0.348 |
| C | 100 | 0.051 | 0.050 | 0.050 | 0.134 | 0.134 | 0.133 | 0.218 | 0.218 | 0.217 |
|  | 110 | 0.061 | 0.061 | 0.060 | 0.162 | 0.162 | 0.161 | 0.264 | 0.263 | 0.263 |
|  | 120 | 0.073 | 0.072 | 0.072 | 0.193 | 0.193 | 0.192 | 0.314 | 0.313 | 0.313 |
|  | 130 | 0.086 | 0.085 | 0.084 | 0.227 | 0.226 | 0.225 | 0.368 | 0.368 | 0.367 |
|  | 140 | 0.099 | 0.099 | 0.097 | 0.263 | 0.263 | 0.261 | 0.427 | 0.427 | 0.425 |
|  | 150 | 0.114 | 0.113 | 0.112 | 0.302 | 0.301 | 0.300 | 0.490 | 0.490 | 0.488 |
| Notes: |  |  |  |  |  |  |  |  |  |  |

1.	The cumulative shear wall segment length for each side of the building shall be equal to or greater than the tabular shear wall length required.  If the required shear wall segment length provided is not one continuous shear wall segment, the total shear wall length required shall be increased by 0.67 feet (8 inches) for each additional shear wall segment making up the total shear wall length on a side.

2.	The minimum shear wall segment length shall be 2 feet-0 inches.   Values less than 2 feet-0 inches are shown only for summation of shear wall segments and for interpolation purposes.  A grouted cell with vertical reinforcement of the size indicated is required at each end of every shear wall segment.

3.   Other than incidental utility penetrations, shearwall piers and shearwall segments shall not contain openings with a maximum horizontal or vertical dimension of 5 inches for piers and 12 inches for portions of shearwall segments above and below piers. The total area of openings in any one segment of shearwall shall not exceed 144 square inches.

4.	Required shearwall lengths normal (perpendicular) to the ridge are per lineal foot of building length. Multiply tabular values by building length (distance between adjacent shear walls perpendicular to the ridge if interior shear walls are used for total shear wall length required.

5.	Shear wall lengths are based on shear wall segment heights of 80 inches (height from the floor to the top of the highest opening adjacent to the shear segment—corners and openings as permitted by Note 3 of this table are not considered for the purpose of this measurement). For shear segment heights other than 80 inches, multiply tabular length values as follows:

| Segment Height (inches) | Length Multiplier |
| --- | --- |
| 88 | 1.09 |
| 96 | 1.19 |
| 104 | 1.28 |
| 112 | 1.37 |

Table R609.5.1E Grade 60, revise text to read as follows:

| TABLE R609.5.1E Grade 60 |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| REQUIRED SHEARWALL LENGTH PERPENDICULAR TO RIDGE - NO. 4 REINFORCEMENT |  |  |  |  |  |  |  |  |  |  |
| PER FOOT OF BUILDING LENGTH1,2,3,4,5 |  |  |  |  |  |  |  |  |  |  |
| ROOF ANGLE 30° |  |  |  |  |  |  |  |  |  |  |
| TOP STORY |  |  |  |  | 1ST STORY OF 2 STORY OR 2ND STORY OF 3 STORY |  |  | 1ST STORY OF 3 STORY |  |  |
| Exp-osure | Wind Speed | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  |
|  |  | 24 | 32 | 40 | 24 | 32 | 40 | 24 | 32 | 40 |
| B | 100 | 0.088 | 0.102 | 0.117 | 0.166 | 0.180 | 0.195 | 0.243 | 0.257 | 0.272 |
|  | 110 | 0.107 | 0.124 | 0.142 | 0.201 | 0.217 | 0.236 | 0.294 | 0.311 | 0.329 |
|  | 120 | 0.127 | 0.147 | 0.169 | 0.239 | 0.259 | 0.280 | 0.350 | 0.371 | 0.392 |
|  | 130 | 0.149 | 0.173 | 0.198 | 0.280 | 0.304 | 0.329 | 0.411 | 0.435 | 0.460 |
|  | 140 | 0.173 | 0.200 | 0.230 | 0.325 | 0.352 | 0.382 | 0.477 | 0.504 | 0.534 |
|  | 150 | 0.199 | 0.230 | 0.264 | 0.373 | 0.404 | 0.438 | 0.548 | 0.579 | 0.613 |
| C | 100 | 0.124 | 0.143 | 0.164 | 0.232 | 0.252 | 0.273 | 0.341 | 0.361 | 0.382 |
|  | 110 | 0.150 | 0.173 | 0.199 | 0.281 | 0.305 | 0.330 | 0.413 | 0.437 | 0.462 |
|  | 120 | 0.178 | 0.206 | 0.237 | 0.335 | 0.363 | 0.393 | 0.491 | 0.519 | 0.550 |
|  | 130 | 0.209 | 0.242 | 0.278 | 0.393 | 0.426 | 0.461 | 0.577 | 0.610 | 0.645 |
|  | 140 | 0.242 | 0.281 | 0.322 | 0.456 | 0.494 | 0.535 | 0.669 | 0.707 | 0.748 |
|  | 150 | 0.278 | 0.322 | 0.370 | 0.523 | 0.567 | 0.614 | 0.768 | 0.812 | 0.859 |
| REQUIRED SHEARWALL LENGTH PERPENDICULAR TO RIDGE - NO. 5 REINFORCEMENT |  |  |  |  |  |  |  |  |  |  |
| PER FOOT OF BUILDING LENGTH1,2,3,4,6 |  |  |  |  |  |  |  |  |  |  |
| ROOF ANGLE 30° |  |  |  |  |  |  |  |  |  |  |
| TOP STORY |  |  |  |  | 1ST STORY OF 2 STORY OR 2ND STORY OF 3 STORY |  |  | 1ST STORY OF 3 STORY |  |  |
| Exp-osure | Wind Speed | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  |
|  |  | 24 | 32 | 40 | 24 | 32 | 40 | 24 | 32 | 40 |
| B | 100 | 0.059 | 0.069 | 0.079 | 0.112 | 0.121 | 0.131 | 0.164 | 0.173 | 0.183 |
|  | 110 | 0.072 | 0.083 | 0.095 | 0.135 | 0.146 | 0.159 | 0.198 | 0.210 | 0.222 |
|  | 120 | 0.086 | 0.099 | 0.114 | 0.161 | 0.174 | 0.189 | 0.236 | 0.249 | 0.264 |
|  | 130 | 0.100 | 0.116 | 0.133 | 0.189 | 0.204 | 0.222 | 0.277 | 0.293 | 0.310 |
|  | 140 | 0.116 | 0.135 | 0.155 | 0.219 | 0.237 | 0.257 | 0.321 | 0.339 | 0.359 |
|  | 150 | 0.134 | 0.155 | 0.177 | 0.251 | 0.272 | 0.295 | 0.369 | 0.390 | 0.412 |
| C | 100 | 0.083 | 0.096 | 0.111 | 0.156 | 0.170 | 0.184 | 0.230 | 0.243 | 0.257 |
|  | 110 | 0.101 | 0.117 | 0.134 | 0.189 | 0.205 | 0.222 | 0.278 | 0.294 | 0.311 |
|  | 120 | 0.120 | 0.139 | 0.159 | 0.225 | 0.244 | 0.265 | 0.331 | 0.350 | 0.370 |
|  | 130 | 0.141 | 0.163 | 0.187 | 0.264 | 0.287 | 0.311 | 0.388 | 0.410 | 0.434 |
|  | 140 | 0.163 | 0.189 | 0.217 | 0.307 | 0.333 | 0.360 | 0.450 | 0.476 | 0.504 |
|  | 150 | 0.187 | 0.217 | 0.249 | 0.352 | 0.382 | 0.413 | 0.517 | 0.546 | 0.578 |
| Notes: |  |  |  |  |  |  |  |  |  |  |

1.	The cumulative shear wall segment length for each side of the building shall be equal to or greater than the tabular shear wall length required.  If the required shear wall segment length provided is not one continuous shear wall segment, the total shear wall length required shall be increased by 0.67 feet (8 inches) for each additional shear wall segment making up the total shear wall length on a side.

2.	The minimum shear wall segment length shall be 2 feet-0 inches.   Values less than 2 feet-0 inches are shown only for summation of shear wall segments and for interpolation purposes.  FilledA grouted cell with vertical reinforcement of the size indicated is required at each end of every shear wall segment.

3.    Other than incidental utility penetrations, shearwall piers and shearwall segments shall not contain openings with a maximum horizontal or vertical dimension of 5 inches for piers and 12 inches for portions of shearwall segments above and below piers. The total area of openings in any one segment of shearwall shall not exceed 144 square inches.

4.	Required shearwall lengths normal (perpendicular) to the ridge are per lineal foot of building length. Multiply tabular values by building length (distance between adjacent shear walls perpendicular to the ridge if interior shear walls are used for total shear wall length required.

5.	Shear wall lengths are based on shear wall segment heights of 80 inches (height from the floor to the top of the highest opening adjacent to the shear segment—corners and openings as permitted by Note 3 of this table are not considered for the purpose of this measurement). For shear segment heights other than 80 inches, multiply tabular length values as follows:

| Segment Height (inches) | Length Multiplier |
| --- | --- |
| 88 | 1.09 |
| 96 | 1.19 |
| 104 | 1.28 |
| 112 | 1.37 |

Table R609.5.1F Grade 60, revise text to read as follows:

| TABLE R609.5.1F Grade 60 |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| REQUIRED SHEARWALL LENGTH PERPENDICULAR TO RIDGE - NO. 4 REINFORCEMENT |  |  |  |  |  |  |  |  |  |  |
| PER FOOT OF BUILDING LENGTH1,2,3,4,5 |  |  |  |  |  |  |  |  |  |  |
| ROOF ANGLE 45° |  |  |  |  |  |  |  |  |  |  |
| TOP STORY |  |  |  |  | 1ST STORY OF 2 STORY OR 2ND STORY OF 3 STORY |  |  | 1ST STORY OF 3 STORY |  |  |
| Exp-osure | Wind Speed | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  |
|  |  | 24 | 32 | 40 | 24 | 32 | 40 | 24 | 32 | 40 |
| B | 100 | 0.118 | 0.142 | 0.168 | 0.196 | 0.220 | 0.246 | 0.273 | 0.297 | 0.323 |
|  | 110 | 0.143 | 0.172 | 0.204 | 0.237 | 0.266 | 0.297 | 0.331 | 0.360 | 0.391 |
|  | 120 | 0.170 | 0.205 | 0.242 | 0.282 | 0.317 | 0.354 | 0.393 | 0.428 | 0.466 |
|  | 130 | 0.200 | 0.241 | 0.284 | 0.331 | 0.372 | 0.415 | 0.462 | 0.503 | 0.546 |
|  | 140 | 0.232 | 0.279 | 0.330 | 0.384 | 0.431 | 0.482 | 0.536 | 0.583 | 0.634 |
|  | 150 | 0.266 | 0.320 | 0.378 | 0.440 | 0.495 | 0.553 | 0.615 | 0.669 | 0.727 |
| C | 100 | 0.166 | 0.200 | 0.236 | 0.274 | 0.308 | 0.345 | 0.383 | 0.417 | 0.453 |
|  | 110 | 0.200 | 0.241 | 0.285 | 0.332 | 0.373 | 0.417 | 0.464 | 0.505 | 0.549 |
|  | 120 | 0.239 | 0.287 | 0.340 | 0.395 | 0.444 | 0.496 | 0.552 | 0.600 | 0.653 |
|  | 130 | 0.280 | 0.337 | 0.399 | 0.464 | 0.521 | 0.582 | 0.647 | 0.705 | 0.766 |
|  | 140 | 0.325 | 0.391 | 0.462 | 0.538 | 0.604 | 0.675 | 0.751 | 0.817 | 0.888 |
|  | 150 | 0.373 | 0.449 | 0.531 | 0.617 | 0.694 | 0.775 | 0.862 | 0.938 | 1.020 |
| REQUIRED SHEARWALL LENGTH PERPENDICULAR TO RIDGE - NO. 5 REINFORCEMENT |  |  |  |  |  |  |  |  |  |  |
| PER FOOT OF BUILDING LENGTH1,2,3,4,6 |  |  |  |  |  |  |  |  |  |  |
| ROOF ANGLE 45° |  |  |  |  |  |  |  |  |  |  |
| TOP STORY |  |  |  |  | 1ST STORY OF 2 STORY OR 2ND STORY OF 3 STORY |  |  | 1ST STORY OF 3 STORY |  |  |
| Exp-osure | Wind Speed | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  |
|  |  | 24 | 32 | 40 | 24 | 32 | 40 | 24 | 32 | 40 |
| B | 100 | 0.080 | 0.096 | 0.113 | 0.132 | 0.148 | 0.165 | 0.184 | 0.200 | 0.218 |
|  | 110 | 0.096 | 0.116 | 0.137 | 0.159 | 0.179 | 0.200 | 0.223 | 0.242 | 0.263 |
|  | 120 | 0.115 | 0.138 | 0.163 | 0.190 | 0.213 | 0.238 | 0.265 | 0.288 | 0.313 |
|  | 130 | 0.134 | 0.162 | 0.191 | 0.223 | 0.250 | 0.280 | 0.311 | 0.338 | 0.368 |
|  | 140 | 0.156 | 0.188 | 0.222 | 0.258 | 0.290 | 0.324 | 0.361 | 0.392 | 0.427 |
|  | 150 | 0.179 | 0.216 | 0.255 | 0.296 | 0.333 | 0.372 | 0.414 | 0.450 | 0.490 |
| C | 100 | 0.111 | 0.134 | 0.159 | 0.185 | 0.208 | 0.232 | 0.258 | 0.281 | 0.305 |
|  | 110 | 0.135 | 0.163 | 0.192 | 0.223 | 0.251 | 0.281 | 0.312 | 0.340 | 0.369 |
|  | 120 | 0.161 | 0.193 | 0.229 | 0.266 | 0.299 | 0.334 | 0.371 | 0.404 | 0.439 |
|  | 130 | 0.188 | 0.227 | 0.268 | 0.312 | 0.351 | 0.392 | 0.436 | 0.474 | 0.516 |
|  | 140 | 0.219 | 0.263 | 0.311 | 0.362 | 0.407 | 0.455 | 0.505 | 0.550 | 0.598 |
|  | 150 | 0.251 | 0.302 | 0.357 | 0.416 | 0.467 | 0.522 | 0.580 | 0.632 | 0.687 |
| Notes: |  |  |  |  |  |  |  |  |  |  |

1.	The cumulative shear wall segment length for each side of the building shall be equal to or greater than the tabular shear wall length required.  If the required shear wall segment length provided is not one continuous shear wall segment, the total shear wall length required shall be increased by 0.67 feet (8 inches) for each additional shear wall segment making up the total shear wall length on a side.

2.	The minimum shear wall segment length shall be 2 feet-0 inches.   Values less than 2 feet-0 inches are shown only for summation of shear wall segments and for interpolation purposes.  A grouted cell with vertical reinforcement of the size indicated is required at each end of every shear wall segment.

3.    Other than incidental utility penetrations, shear wall piers and shear wall segments shall not contain openings with a maximum horizontal or vertical dimension of 5 inches for piers and 12 inches for portions of shear wall segments above and below piers. The total area of openings in any one segment of shear wall shall not exceed 144 square inches.

4.	Required shear wall lengths normal (perpendicular) to the ridge are per lineal foot of building length. Multiply tabular values by building length (distance between adjacent shear walls perpendicular to the ridge if interior shear walls are used for total shear wall length required.

5.	Shear wall lengths are based on shear wall segment heights of 80 inches (height from the floor to the top of the highest opening adjacent to the shear segment—corners and openings as permitted by Note 3 of this table are not considered for the purpose of this measurement). For shear segment heights other than 80 inches, multiply tabular length values as follows:

| Segment Height (inches) | Length Multiplier |
| --- | --- |
| 88 | 1.09 |
| 96 | 1.19 |
| 104 | 1.28 |
| 112 | 1.37 |

Table R609.5.1G Grade 40, revise text to read as follows:

| TABLE R609.5.1G GRADE 40 REQUIRED SHEARWALL LENGTH PARALLEL TO RIDGE NO. 4 REINFORCEMENT1,2,3,5 |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | ROOF ANGLE ≤ 230 |  |  |  |  |  |  |  |  |
|  |  | TOP STORY |  |  | 1ST STORY OF 2 STORY OR 2ND STORY OF 3 STORY |  |  | 1ST STORY OF 3 STORY |  |  |
| Exp | Wind Speed | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  |
|  |  | 24 | 32 | 40 | 24 | 32 | 40 | 24 | 32 | 40 |
| B | 100 | 2.32 | 3.31 | 4.51 | 5.29 | 7.15 | 9.31 | 7.77 | 10.45 | 13.55 |
|  | 110 | 2.81 | 4.01 | 5.46 | 6.40 | 8.65 | 11.27 | 9.40 | 12.65 | 16.39 |
|  | 120 | 3.35 | 4.77 | 6.50 | 7.61 | 10.30 | 13.41 | 11.19 | 15.05 | 19.51 |
|  | 130 | 3.93 | 5.59 | 7.63 | 8.94 | 12.09 | 15.74 | 13.13 | 17.67 | 22.90 |
|  | 140 | 4.55 | 6.49 | 8.84 | 10.36 | 14.02 | 18.26 | 15.23 | 20.49 | 26.56 |
|  | 150 | 5.23 | 7.45 | 10.15 | 11.90 | 16.09 | 20.96 | 17.48 | 23.52 | 30.48 |
| C | 100 | 2.75 | 3.98 | 5.49 | 6.98 | 9.52 | 12.49 | 10.85 | 14.57 | 18.85 |
|  | 110 | 3.33 | 4.81 | 6.64 | 8.45 | 11.52 | 15.11 | 13.13 | 17.63 | 22.81 |
|  | 120 | 3.97 | 5.73 | 7.90 | 10.05 | 13.70 | 17.98 | 15.63 | 20.98 | 27.14 |
|  | 130 | 4.66 | 6.72 | 9.27 | 11.80 | 16.08 | 21.10 | 18.34 | 24.63 | 31.86 |
|  | 140 | 5.40 | 7.79 | 10.75 | 13.68 | 18.65 | 24.47 | 21.27 | 28.56 | 36.95 |
|  | 150 | 6.20 | 8.95 | 12.34 | 15.71 | 21.41 | 28.10 | 24.42 | 32.79 | 42.41 |

Notes :

1.  The cumulative shear wall segment length for each side of the building shall be equal to or greater than the tabular shear wall length required. If the required shear wall segment length provided is not continuous the total shear wall length required shall be increased by 8" for each additional shear wall segment on a side.

2.  Minimum shear wall segment length shall be 2'-0". A grouted cell with reinforcing steel shall be provided at each end of every shear wall segment. A minimum length of 24 inches (610 mm) of solid wall segment, extending the full height of each wall, shall be provided at exterior corners of exterior walls. A fully grouted cell with reinforcing steel shall be provided at each end of every shear wall segment.

3.  Portions of walls with openings shall not be considered part of the shear wall length.

4. Required shearwall lengths perpendicular to the ridge are per lineal foot of building length. Multiply tabular values by building length for total shear wall length required.

5. Shearwall lengths for no. 4 reinforcement are based on shearwall segment height of 80 inches and shearwall segment length of 24 inches. Multiply tabular length by shearwall adjustment factor from Table R609.5.1S for other segment lengths and heights.

6. Shearwall lengths for no. 5 reinforcement are based on shearwall segment height of 96 inches and shearwall segment length of 24 inches. Multiply tabular length by shearwall adjustment factor from Table R609.5.1S for other segment height lengths and heights.

Table R609.5.1H Grade 40, revise text to read as follows:

| TABLE R609.5.1H GRADE 40 REQUIRED SHEARWALL LENGTH PARALLEL TO RIDGE NO. 5 REINFORCEMENT1,2,3,6 |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | ROOF ANGLE ≤ 230 |  |  |  |  |  |  |  |  |
|  |  | TOP STORY |  |  | 1ST STORY OF 2 STORY OR 2ND STORY OF 3 STORY |  |  | 1ST STORY OF 3 STORY |  |  |
| Exp | Wind Speed | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  |
|  |  | 24 | 32 | 40 | 24 | 32 | 40 | 24 | 32 | 40 |
| B | 100 | 1.59 | 2.26 | 3.08 | 3.61 | 4.88 | 6.36 | 5.30 | 7.14 | 9.25 |
|  | 110 | 1.92 | 2.73 | 3.73 | 4.37 | 5.91 | 7.69 | 6.42 | 8.63 | 11.19 |
|  | 120 | 2.28 | 3.25 | 4.44 | 5.20 | 7.03 | 9.16 | 7.64 | 10.28 | 13.32 |
|  | 130 | 2.68 | 3.82 | 5.21 | 6.10 | 8.25 | 10.75 | 8.96 | 12.06 | 15.63 |
|  | 140 | 3.11 | 4.43 | 6.04 | 7.07 | 9.57 | 12.46 | 10.40 | 13.99 | 18.13 |
|  | 150 | 3.57 | 5.08 | 6.93 | 8.12 | 10.99 | 14.31 | 11.93 | 16.06 | 20.81 |
| C | 100 | 1.88 | 2.71 | 3.75 | 4.77 | 6.50 | 8.52 | 7.41 | 9.95 | 12.87 |
|  | 110 | 2.28 | 3.28 | 4.53 | 5.77 | 7.86 | 10.31 | 8.96 | 12.04 | 15.57 |
|  | 120 | 2.71 | 3.91 | 5.39 | 6.86 | 9.36 | 12.28 | 10.67 | 14.32 | 18.53 |
|  | 130 | 3.18 | 4.59 | 6.33 | 8.05 | 10.98 | 14.41 | 12.52 | 16.81 | 21.75 |
|  | 140 | 3.69 | 5.32 | 7.34 | 9.34 | 12.73 | 16.71 | 14.52 | 19.50 | 25.22 |
|  | 150 | 4.23 | 6.11 | 8.43 | 10.72 | 14.62 | 19.18 | 16.67 | 22.38 | 28.95 |

Notes :

1.  The cumulative shear wall segment length for each side of the building shall be equal to or greater than the tabular shear wall length required.  If the required shear wall segment length provided is not continuous the total shear wall length required shall be increased by 8" for each additional shear wall segment on a side.

2.  Minimum shear wall segment length shall be 2'-0". A grouted cell with reinforcing steel shall be provided at each end of every shear wall segment. A minimum length of 24 inches (610 mm) of solid wall segment, extending the full height of each wall, shall be provided at exterior corners of exterior walls. A fully grouted cell with reinforcing steel shall be provided at each end of every shear wall segment.

3.  Portions of walls with openings shall not be considered part of the shear wall length.

4. Required shearwall lengths perpendicular to the ridge are per lineal foot of building length. Multiply tabular values by building length for total shear wall length required.

5. Shearwall lengths for no. 4 reinforcement are based on shearwall segment height of 80 inches and shearwall segment length of 24 inches. Multiply tabular length by shearwall adjustment factor from Table R609.5.1S for other segment lengths and heights.

6. Shearwall lengths for no. 5 reinforcement are based on shearwall segment height of 96 inches and  shearwall segment length of 24 inches. Multiply tabular length by shearwall adjustment factor from Table R609.5.1S for other segment height lengths and heights.

Table R609.5.1I Grade 40, revise text to read as follows:

| TABLE R609.5.1I GRADE 40 REQUIRED SHEARWALL LENGTH PARALLEL TO RIDGE NO. 4 REINFORCEMENT1,2,3,5 |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | ROOF ANGLE 300 |  |  |  |  |  |  |  |  |
|  |  | TOP STORY |  |  | 1ST STORY OF 2 STORY OR 2ND STORY OF 3 STORY |  |  | 1ST STORY OF 3 STORY |  |  |
| Exp | Wind Speed | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  |
|  |  | 24 | 32 | 40 | 24 | 32 | 40 | 24 | 32 | 40 |
| B | 100 | 2.39 | 3.51 | 4.88 | 5.10 | 7.07 | 9.32 | 7.44 | 10.24 | 13.44 |
|  | 110 | 2.89 | 4.25 | 5.90 | 6.17 | 8.55 | 11.28 | 9.00 | 12.39 | 16.26 |
|  | 120 | 3.43 | 5.06 | 7.02 | 7.35 | 10.18 | 13.43 | 10.71 | 14.75 | 19.35 |
|  | 130 | 4.03 | 5.94 | 8.24 | 8.62 | 11.95 | 15.76 | 12.57 | 17.31 | 22.71 |
|  | 140 | 4.67 | 6.89 | 9.56 | 10.00 | 13.86 | 18.28 | 14.58 | 20.08 | 26.34 |
|  | 150 | 5.37 | 7.90 | 10.98 | 11.48 | 15.91 | 20.98 | 16.74 | 23.05 | 30.23 |
| C | 100 | 2.87 | 4.29 | 6.05 | 6.79 | 9.51 | 12.66 | 10.37 | 14.24 | 18.63 |
|  | 110 | 3.47 | 5.19 | 7.32 | 8.22 | 11.51 | 15.32 | 12.55 | 17.23 | 22.54 |
|  | 120 | 4.13 | 6.18 | 8.71 | 9.78 | 13.69 | 18.23 | 14.93 | 20.51 | 26.83 |
|  | 130 | 4.85 | 7.26 | 10.23 | 11.48 | 16.07 | 21.40 | 17.53 | 24.06 | 31.49 |
|  | 140 | 5.62 | 8.41 | 11.86 | 13.31 | 18.64 | 24.82 | 20.33 | 27.91 | 36.52 |
|  | 150 | 6.45 | 9.66 | 13.62 | 15.28 | 21.39 | 28.49 | 23.33 | 32.04 | 41.92 |

Notes :

1.  The cumulative shear wall segment length for each side of the building shall be equal to or greater than the tabular shear wall length required.  If the required shear wall segment length provided is not continuous the total shear wall length required shall be increased by 8" for each additional shear wall segment on a side.

2.  Minimum shear wall segment length shall be 2'-0". A grouted cell with reinforcing steel shall be provided at each end of every shear wall segment. A minimum length of 24 inches (610 mm) of solid wall segment, extending the full height of each wall, shall be provided at exterior corners of exterior walls. A fully grouted cell with reinforcing steel shall be provided at each end of every shear wall segment.

3.  Portions of walls with openings shall not be considered part of the shear wall length.

4. Required shearwall lengths perpendicular to the ridge are per lineal foot of building length. Multiply tabular values by building length for total shear wall length required.

5. Shearwall lengths for no. 4 reinforcement are based on shearwall segment height of 80 inches and  shearwall segment length of 24 inches.  Multiply tabular length by shearwall adjustment factor from Table R609.5.1S for other segment lengths and heights.

6. Shearwall lengths for no. 5 reinforcement are based on shearwall segment height of 96 inches  and  shearwall segment length of 24 inches.  Multiply tabular length by shearwall adjustment factor from Table R609.5.1S for other segment height lengths and heights.

Table R609.5.1J Grade 40, revise text to read as follows:

| TABLE R609.5.1J GRADE 40 REQUIRED SHEARWALL LENGTH PARALLEL TO RIDGE NO. 5 REINFORCEMENT1,2,3,6 |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | ROOF ANGLE 300 |  |  |  |  |  |  |  |  |
|  |  | TOP STORY |  |  | 1ST STORY OF 2 STORY OR 2ND STORY OF 3 STORY |  |  | 1ST STORY OF 3 STORY |  |  |
| Exp | Wind Speed | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  |
|  |  | 24 | 32 | 40 | 24 | 32 | 40 | 24 | 32 | 40 |
| B | 100 | 1.63 | 2.40 | 3.33 | 3.48 | 4.83 | 6.37 | 5.08 | 6.99 | 9.17 |
|  | 110 | 1.97 | 2.90 | 4.03 | 4.21 | 5.84 | 7.70 | 6.15 | 8.46 | 11.10 |
|  | 120 | 2.34 | 3.45 | 4.80 | 5.02 | 6.95 | 9.17 | 7.31 | 10.07 | 13.21 |
|  | 130 | 2.75 | 4.05 | 5.63 | 5.89 | 8.16 | 10.76 | 8.58 | 11.82 | 15.50 |
|  | 140 | 3.19 | 4.70 | 6.53 | 6.83 | 9.46 | 12.48 | 9.96 | 13.71 | 17.98 |
|  | 150 | 3.66 | 5.40 | 7.49 | 7.84 | 10.86 | 14.32 | 11.43 | 15.73 | 20.64 |
| C | 100 | 1.96 | 2.93 | 4.13 | 4.64 | 6.49 | 8.64 | 7.08 | 9.72 | 12.72 |
|  | 110 | 2.37 | 3.55 | 5.00 | 5.61 | 7.85 | 10.46 | 8.57 | 11.76 | 15.39 |
|  | 120 | 2.82 | 4.22 | 5.95 | 6.68 | 9.35 | 12.45 | 10.19 | 14.00 | 18.31 |
|  | 130 | 3.31 | 4.95 | 6.98 | 7.84 | 10.97 | 14.61 | 11.96 | 16.43 | 21.49 |
|  | 140 | 3.84 | 5.74 | 8.10 | 9.09 | 12.72 | 16.94 | 13.88 | 19.05 | 24.93 |
|  | 150 | 4.41 | 6.59 | 9.29 | 10.43 | 14.61 | 19.45 | 15.93 | 21.87 | 28.62 |

Notes:

1.  The cumulative shear wall segment length for each side of the building shall be equal to or greater than the tabular shear wall length required. If the required shear wall segment length provided is not continuous the total shear wall length required shall be increased by 8" for each additional shear wall segment on a side.

2.  Minimum shear wall segment length shall be 2'-0". A grouted cell with reinforcing steel shall be provided at each end of every shear wall segment. A minimum length of 24 inches (610 mm) of solid wall segment, extending the full height of each wall, shall be provided at exterior corners of exterior walls. A fully grouted cell with reinforcing steel shall be provided at each end of every shear wall segment.

3.  Portions of walls with openings shall not be considered part of the shear wall length.

4. Required shearwall lengths perpendicular to the ridge are per lineal foot of building length. Multiply tabular values by building length for total shear wall length required.

5. Shearwall lengths for no. 4 reinforcement are based on shearwall segment height of 80 inches and shearwall segment length of 24 inches. Multiply tabular length by shearwall adjustment factor from Table R609.5.1S for other segment lengths and heights.

6. Shearwall lengths for no. 5 reinforcement are based on shearwall segment height of 96 inches and shearwall segment length of 24 inches. Multiply tabular length by shearwall adjustment factor from Table R609.5.1S for other segment height lengths and heights.

Table R609.5.1K Grade 40, revise text to read as follows:

| TABLE R609.5.1K GRADE 40 REQUIRED SHEARWALL LENGTH PARALLEL TO RIDGE NO. 4 REINFORCEMENT1,2,3,5 |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | ROOF ANGLE 450 |  |  |  |  |  |  |  |  |
|  |  | TOP STORY |  |  | 1ST STORY OF 2 STORY OR 2ND STORY OF 3 STORY |  |  | 1ST STORY OF 3 STORY |  |  |
| Exp | Wind Speed | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  |
|  |  | 24 | 32 | 40 | 24 | 32 | 40 | 24 | 32 | 40 |
| B | 100 | 3.04 | 4.65 | 6.66 | 3.04 | 8.21 | 11.11 | 8.28 | 11.74 | 15.80 |
|  | 110 | 3.68 | 5.63 | 8.06 | 6.96 | 9.93 | 13.44 | 10.02 | 14.20 | 19.12 |
|  | 120 | 4.37 | 6.70 | 9.59 | 8.29 | 11.82 | 15.99 | 11.93 | 16.90 | 22.76 |
|  | 130 | 5.13 | 7.86 | 11.25 | 9.72 | 13.87 | 18.77 | 14.00 | 19.84 | 26.71 |
|  | 140 | 5.95 | 9.12 | 13.05 | 11.28 | 16.09 | 21.77 | 16.24 | 23.01 | 30.97 |
|  | 150 | 6.83 | 10.47 | 14.98 | 12.95 | 18.47 | 24.99 | 18.64 | 26.41 | 35.56 |
| C | 100 | 3.78 | 5.93 | 8.66 | 7.83 | 11.34 | 15.57 | 10.37 | 14.24 | 18.63 |
|  | 110 | 4.57 | 7.17 | 10.48 | 9.47 | 13.73 | 18.84 | 12.55 | 17.23 | 22.54 |
|  | 120 | 5.44 | 8.53 | 12.47 | 11.27 | 16.34 | 22.42 | 14.93 | 20.51 | 26.83 |
|  | 130 | 6.39 | 10.01 | 14.64 | 13.23 | 19.17 | 26.31 | 17.53 | 24.06 | 31.49 |
|  | 140 | 7.41 | 11.61 | 16.98 | 15.34 | 22.24 | 30.52 | 20.33 | 27.91 | 36.52 |
|  | 150 | 8.50 | 13.33 | 19.49 | 17.61 | 25.53 | 35.03 | 23.33 | 32.04 | 41.92 |

Notes:

1.  The cumulative shear wall segment length for each side of the building shall be equal to or greater than the tabular shear wall length required. If the required shear wall segment length provided is not continuous the total shear wall length required shall be increased by 8" for each additional shear wall segment on a side.

2.  Minimum shear wall segment length shall be 2'-0". A grouted cell with reinforcing steel shall be provided at each end of every shear wall segment. A minimum length of 24 inches (610 mm) of solid wall segment, extending the full height of each wall, shall be provided at exterior corners of exterior walls. A fully grouted cell with reinforcing steel shall be provided at each end of every shear wall segment.

3.  Portions of walls with openings shall not be considered part of the shear wall length.

4. Required shearwall lengths perpendicular to the ridge are per lineal foot of building length. Multiply tabular values by building length for total shear wall required.

5. Shearwall lengths for no. 4 reinforcement are based on shearwall segment height of 80 inches and shearwall segment length of 24 inches. Multiply tabular length by shearwall adjustment factor from Table R609.5.1S for other segment lengths and heights.

6. Shearwall lengths for no. 5 reinforcement are based on shearwall segment height of 96 inches and shearwall segment length of 24 inches. Multiply tabular length by shearwall adjustment factor from Table R609.5.1S for other segment height lengths and heights.

Table R609.5.1L Grade 40, revise text to read as follows:

| TABLE R609.5.1L GRADE 40 REQUIRED SHEARWALL LENGTH PARALLEL TO RIDGE NO. 5 REINFORCEMENT1,2,3,6 |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | ROOF ANGLE 450 |  |  |  |  |  |  |  |  |
|  |  | TOP STORY |  |  | 1ST STORY OF 2 STORY OR 2ND STORY OF 3 STORY |  |  | 1ST STORY OF 3 STORY |  |  |
| Exp | Wind Speed | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  |
|  |  | 24 | 32 | 40 | 24 | 32 | 40 | 24 | 32 | 40 |
| B | 100 | 2.07 | 3.18 | 4.55 | 3.93 | 5.60 | 7.58 | 5.66 | 8.01 | 10.79 |
|  | 110 | 2.51 | 3.84 | 5.50 | 4.75 | 6.78 | 9.17 | 6.84 | 9.70 | 13.05 |
|  | 120 | 2.99 | 4.57 | 6.55 | 5.66 | 8.07 | 10.92 | 8.14 | 11.54 | 15.54 |
|  | 130 | 3.50 | 5.37 | 7.68 | 6.64 | 9.47 | 12.81 | 9.56 | 13.54 | 18.23 |
|  | 140 | 4.06 | 6.23 | 8.91 | 7.70 | 10.99 | 14.86 | 11.08 | 15.71 | 21.15 |
|  | 150 | 4.67 | 7.15 | 10.23 | 8.84 | 12.61 | 17.06 | 12.72 | 18.03 | 24.27 |
| C | 100 | 2.58 | 4.05 | 5.91 | 5.34 | 7.74 | 10.63 | 7.84 | 11.06 | 14.83 |
|  | 110 | 3.12 | 4.89 | 7.15 | 6.47 | 9.37 | 12.86 | 9.48 | 13.38 | 17.94 |
|  | 120 | 3.71 | 5.83 | 8.51 | 7.69 | 11.15 | 15.31 | 11.29 | 15.93 | 21.36 |
|  | 130 | 4.36 | 6.84 | 9.99 | 9.03 | 13.09 | 17.96 | 13.25 | 18.69 | 25.06 |
|  | 140 | 5.06 | 7.93 | 11.59 | 10.47 | 15.18 | 20.83 | 15.36 | 21.68 | 29.07 |
|  | 150 | 5.80 | 9.10 | 13.30 | 12.02 | 17.43 | 23.92 | 17.63 | 24.88 | 33.37 |

Notes:

1.  The cumulative shear wall segment length for each side of the building shall be equal to or greater than the tabular shear wall length required.  If the required shear wall segment length provided is not continuous the total shear wall length required shall be increased by 8" for each additional shear wall segment on a side.

2.  Minimum shear wall segment length shall be 2'-0". A grouted cell with reinforcing steel shall be provided at each end of every shear wall segment. A minimum length of 24 inches (610 mm) of solid wall segment, extending the full height of each wall, shall be provided at exterior corners of exterior walls. A fully grouted cell with reinforcing steel shall be provided at each end of every shear wall segment.

3.  Portions of walls with openings shall not be considered part of the shear wall length.

4. Required shearwall lengths perpendicular to the ridge are per lineal foot of building length. Multiply tabular values by building length for total shear wall length.

5. Shearwall lengths for no. 4 reinforcement are based on shearwall segment height of 80 inches and shearwall segment length of 24 inches. Multiply tabular length by shearwall adjustment factor from Table R609.5.1S for other segment lengths and heights.

6. Shearwall lengths for no. 5 reinforcement are based on shearwall segment height of 96 inches and shearwall segment length of 24 inches. Multiply tabular length by shearwall adjustment factor from Table R609.5.1S for other segment height lengths and heights.

Table R609.5.1M Grade 40, revise text to read as follows:

| TABLE R609.5.1M GRADE 40 REQUIRED SHEARWALL LENGTH PERPENDICULAR TO RIDGE NO. 4 REINFORCEMENT PER FOOT OF BUILDING LENGTH1,2,3,4,5 |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ROOF ANGLE ≤ 230 |  |  |  |  |  |  |  |  |  |  |
|  |  | TOP STORY |  |  | 1ST STORY OF 2 STORY OR 2ND STORY OF 3 STORY |  |  | 1ST STORY OF 3 STORY |  |  |
| Exp | Wind Speed | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  |
|  |  | 24 | 32 | 40 | 24 | 32 | 40 | 24 | 32 | 40 |
| B | 100 | 0.077 | 0.077 | 0.076 | 0.204 | 0.204 | 0.203 | 0.332 | 0.331 | 0.330 |
|  | 110 | 0.093 | 0.093 | 0.092 | 0.247 | 0.247 | 0.246 | 0.401 | 0.401 | 0.400 |
|  | 120 | 0.111 | 0.110 | 0.109 | 0.294 | 0.294 | 0.292 | 0.478 | 0.477 | 0.476 |
|  | 130 | 0.130 | 0.129 | 0.128 | 0.345 | 0.345 | 0.343 | 0.561 | 0.560 | 0.558 |
|  | 140 | 0.151 | 0.150 | 0.148 | 0.400 | 0.400 | 0.398 | 0.650 | 0.649 | 0.647 |
|  | 150 | 0.173 | 0.172 | 0.170 | 0.460 | 0.459 | 0.457 | 0.746 | 0.745 | 0.743 |
| C | 100 | 0.108 | 0.107 | 0.106 | 0.286 | 0.286 | 0.285 | 0.465 | 0.464 | 0.463 |
|  | 110 | 0.131 | 0.130 | 0.128 | 0.347 | 0.346 | 0.344 | 0.563 | 0.562 | 0.560 |
|  | 120 | 0.155 | 0.155 | 0.153 | 0.413 | 0.412 | 0.410 | 0.670 | 0.669 | 0.667 |
|  | 130 | 0.182 | 0.181 | 0.179 | 0.484 | 0.483 | 0.481 | 0.786 | 0.785 | 0.783 |
|  | 140 | 0.212 | 0.210 | 0.208 | 0.562 | 0.560 | 0.558 | 0.911 | 0.910 | 0.908 |
|  | 150 | 0.243 | 0.242 | 0.239 | 0.645 | 0.643 | 0.640 | 1.046 | 1.045 | 1.042 |

Notes:

1.  The cumulative shear wall segment length for each side of the building shall be equal to or greater than the tabular shear wall length required.  If the required shear wall segment length provided is not continuous the total shear wall length required shall be increased by 8" for each additional shear wall segment on a side.

2.  Minimum shear wall segment length shall be 2'-0". A grouted cell with reinforcing steel shall be provided at each end of every shear wall segment. A minimum length of 24 inches (610 mm) of solid wall segment, extending the full height of each wall, shall be provided at exterior corners of exterior walls. A fully grouted cell with reinforcing steel shall be provided at each end of every shear wall segment.

3.  Portions of walls with openings shall not be considered part of the shear wall length.

4. Required shearwall lengths perpendicular to the ridge are per lineal foot of building length. Multiply tabular values by building length for total shear wall length.

5. Shearwall lengths for no. 4 reinforcement are based on shearwall segment height of 80 inches and shearwall segment length of 24 inches. Multiply tabular length by shearwall adjustment factor from Table R609.5.1S for other segment lengths and heights.

6. Shearwall lengths for no. 5 reinforcement are based on shearwall segment height of 96 inches and shearwall segment length of 24 inches. Multiply tabular length by shearwall adjustment factor from Table R609.5.1S for other segment height lengths and heights.

Table R609.5.1N Grade 40, revise text to read as follows:

| TABLE R609.5.1N GRADE 40 REQUIRED SHEARWALL LENGTH PERPENDICULAR TO RIDGE NO. 5 REINFORCEMENT PER FOOT OF BUILDING LENGTH1,2,3,4,6 |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ROOF ANGLE ≤ 230 |  |  |  |  |  |  |  |  |  |  |
|  |  | TOP STORY |  |  | 1ST STORY OF 2 STORY OR 2ND STORY OF 3 STORY |  |  | 1ST STORY OF 3 STORY |  |  |
| Exp | Wind Speed | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  |
|  |  | 24 | 32 | 40 | 24 | 32 | 40 | 24 | 32 | 40 |
| B | 100 | 0.053 | 0.052 | 0.052 | 0.139 | 0.139 | 0.139 | 0.226 | 0.226 | 0.226 |
|  | 110 | 0.064 | 0.063 | 0.063 | 0.169 | 0.168 | 0.168 | 0.274 | 0.274 | 0.273 |
|  | 120 | 0.076 | 0.075 | 0.074 | 0.201 | 0.200 | 0.200 | 0.326 | 0.326 | 0.325 |
|  | 130 | 0.089 | 0.088 | 0.087 | 0.236 | 0.235 | 0.234 | 0.383 | 0.382 | 0.381 |
|  | 140 | 0.103 | 0.102 | 0.101 | 0.273 | 0.273 | 0.272 | 0.444 | 0.443 | 0.442 |
|  | 150 | 0.118 | 0.118 | 0.116 | 0.314 | 0.313 | 0.312 | 0.509 | 0.509 | 0.507 |
| C | 100 | 0.074 | 0.073 | 0.072 | 0.196 | 0.195 | 0.194 | 0.317 | 0.317 | 0.316 |
|  | 110 | 0.089 | 0.089 | 0.088 | 0.237 | 0.236 | 0.235 | 0.384 | 0.384 | 0.383 |
|  | 120 | 0.106 | 0.106 | 0.104 | 0.282 | 0.281 | 0.280 | 0.457 | 0.457 | 0.455 |
|  | 130 | 0.125 | 0.124 | 0.122 | 0.331 | 0.330 | 0.328 | 0.536 | 0.536 | 0.534 |
|  | 140 | 0.144 | 0.144 | 0.142 | 0.383 | 0.383 | 0.381 | 0.622 | 0.621 | 0.620 |
|  | 150 | 0.166 | 0.165 | 0.163 | 0.440 | 0.439 | 0.437 | 0.714 | 0.713 | 0.711 |

Notes:

1.  The cumulative shear wall segment length for each side of the building shall be equal to or greater than the tabular shear wall length required.  If the required shear wall segment length provided is not continuous the total shear wall length required shall be increased by 8" for each additional shear wall segment on a side.

2.  Minimum shear wall segment length shall be 2'-0". A grouted cell with reinforcing steel shall be provided at each end of every shear wall segment. A minimum length of 24 inches (610 mm) of solid wall segment, extending the full height of each wall, shall be provided at exterior corners of exterior walls. A fully grouted cell with reinforcing steel shall be provided at each end of every shear wall segment.

3.  Portions of walls with openings shall not be considered part of the shear wall length.

4. Required shearwall lengths perpendicular to the ridge are per lineal foot of building length. Multiply tabular values by building length for total shear wall length.

5. Shearwall lengths for no. 4 reinforcement are based on shearwall segment height of 80 inches and shearwall segment length of 24 inches. Multiply tabular length by shearwall adjustment factor from Table R609.5.1S for other segment lengths and heights.

6. Shearwall lengths for no. 5 reinforcement are based on shearwall segment height of 96 inches and shearwall segment length of 24 inches. Multiply tabular length by shearwall adjustment factor from Table R609.5.1S for other segment height lengths and heights.

Table R609.5.1O Grade 40, revise text to read as follows:

| TABLE R609.5.1O GRADE 40 REQUIRED SHEARWALL LENGTH PERPENDICULAR TO RIDGE NO. 4 REINFORCEMENT PER FOOT OF BUILDING LENGTH1,2,3,4,5 |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ROOF ANGLE 30o |  |  |  |  |  |  |  |  |  |  |
|  |  | TOP STORY |  |  | 1ST STORY OF 2 STORY OR 2ND STORY OF 3 STORY |  |  | 1ST STORY OF 3 STORY |  |  |
| Exp | Wind Speed | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  |
|  |  | 24 | 32 | 40 | 24 | 32 | 40 | 24 | 32 | 40 |
| B | 100 | 0.127 | 0.147 | 0.168 | 0.238 | 0.258 | 0.280 | 0.349 | 0.370 | 0.391 |
|  | 110 | 0.153 | 0.178 | 0.204 | 0.288 | 0.312 | 0.338 | 0.423 | 0.447 | 0.473 |
|  | 120 | 0.182 | 0.211 | 0.242 | 0.343 | 0.372 | 0.403 | 0.503 | 0.532 | 0.563 |
|  | 130 | 0.214 | 0.248 | 0.284 | 0.402 | 0.436 | 0.473 | 0.591 | 0.624 | 0.661 |
|  | 140 | 0.248 | 0.288 | 0.330 | 0.467 | 0.506 | 0.548 | 0.685 | 0.724 | 0.766 |
|  | 150 | 0.285 | 0.330 | 0.379 | 0.536 | 0.581 | 0.629 | 0.786 | 0.831 | 0.880 |
| C | 100 | 0.178 | 0.206 | 0.236 | 0.334 | 0.362 | 0.392 | 0.490 | 0.518 | 0.548 |
|  | 110 | 0.215 | 0.249 | 0.285 | 0.404 | 0.438 | 0.474 | 0.593 | 0.627 | 0.663 |
|  | 120 | 0.256 | 0.296 | 0.340 | 0.481 | 0.521 | 0.565 | 0.706 | 0.746 | 0.789 |
|  | 130 | 0.300 | 0.348 | 0.399 | 0.564 | 0.612 | 0.663 | 0.828 | 0.876 | 0.926 |
|  | 140 | 0.348 | 0.403 | 0.462 | 0.654 | 0.709 | 0.768 | 0.960 | 1.015 | 1.074 |
|  | 150 | 0.400 | 0.463 | 0.531 | 0.751 | 0.814 | 0.882 | 1.102 | 1.166 | 1.233 |

Notes:

1.  The cumulative shear wall segment length for each side of the building shall be equal to or greater than the tabular shear wall length required.  If the required shear wall segment length provided is not continuous the total shear wall length required shall be increased by 8" for each additional shear wall segment on a side.

2.  Minimum shear wall segment length shall be 2'-0". A grouted cell with reinforcing steel shall be provided at each end of every shear wall segment. A minimum length of 24 inches (610 mm) of solid wall segment, extending the full height of each wall, shall be provided at exterior corners of exterior walls. A fully grouted cell with reinforcing steel shall be provided at each end of every shear wall segment.

3.  Portions of walls with openings shall not be considered part of the shear wall length.

4. Required shearwall lengths perpendicular to the ridge are per lineal foot of building length. Multiply tabular values by building length for total shear wall length.

5. Shearwall lengths for no. 4 reinforcement are based on shearwall segment height of 80 inches and shearwall segment length of 24 inches. Multiply tabular length by shearwall adjustment factor from Table R609.5.1S for other segment lengths and heights.

6. Shearwall lengths for no. 5 reinforcement are based on shearwall segment height of 96 inches and shearwall segment length of 24 inches. Multiply tabular length by shearwall adjustment factor from Table R609.5.1S for other segment height lengths and heights.

Table R609.5.1P Grade 40, revise text to read as follows:

| TABLE R609.5.1P GRADE 40 REQUIRED SHEARWALL LENGTH PERPENDICULAR TO RIDGE NO. 5 REINFORCEMENT PER FOOT OF BUILDING LENGTH1,2,3,4,6 |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ROOF ANGLE 30o |  |  |  |  |  |  |  |  |  |  |
|  |  | TOP STORY |  |  | 1ST STORY OF 2 STORY OR 2ND STORY OF 3 STORY |  |  | 1ST STORY OF 3 STORY |  |  |
| Exp | Wind Speed | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  |
|  |  | 24 | 32 | 40 | 24 | 32 | 40 | 24 | 32 | 40 |
| B | 100 | 0.087 | 0.100 | 0.115 | 0.163 | 0.176 | 0.191 | 0.239 | 0.252 | 0.267 |
|  | 110 | 0.105 | 0.121 | 0.139 | 0.197 | 0.213 | 0.231 | 0.289 | 0.305 | 0.323 |
|  | 120 | 0.125 | 0.144 | 0.165 | 0.234 | 0.254 | 0.275 | 0.344 | 0.363 | 0.384 |
|  | 130 | 0.146 | 0.169 | 0.194 | 0.275 | 0.298 | 0.323 | 0.403 | 0.426 | 0.451 |
|  | 140 | 0.170 | 0.196 | 0.225 | 0.319 | 0.345 | 0.374 | 0.468 | 0.494 | 0.523 |
|  | 150 | 0.195 | 0.225 | 0.258 | 0.366 | 0.397 | 0.430 | 0.537 | 0.568 | 0.601 |
| C | 100 | 0.121 | 0.140 | 0.161 | 0.228 | 0.247 | 0.268 | 0.334 | 0.354 | 0.374 |
|  | 110 | 0.147 | 0.170 | 0.195 | 0.276 | 0.299 | 0.324 | 0.405 | 0.428 | 0.453 |
|  | 120 | 0.175 | 0.202 | 0.232 | 0.328 | 0.356 | 0.385 | 0.482 | 0.509 | 0.539 |
|  | 130 | 0.205 | 0.237 | 0.272 | 0.385 | 0.418 | 0.452 | 0.565 | 0.598 | 0.632 |
|  | 140 | 0.238 | 0.275 | 0.316 | 0.447 | 0.484 | 0.525 | 0.656 | 0.693 | 0.734 |
|  | 150 | 0.273 | 0.316 | 0.362 | 0.513 | 0.556 | 0.602 | 0.753 | 0.796 | 0.842 |

Notes:

1.  The cumulative shear wall segment length for each side of the building shall be equal to or greater than the tabular shear wall length required.  If the required shear wall segment length provided is not continuous the total shear wall length required shall be increased by 8" for each additional shear wall segment on a side.

2.  Minimum shear wall segment length shall be 2'-0". A grouted cell with reinforcing steel shall be provided at each end of every shear wall segment. A minimum length of 24 inches (610 mm) of solid wall segment, extending the full height of each wall, shall be provided at exterior corners of exterior walls. A fully grouted cell with reinforcing steel shall be provided at each end of every shear wall segment.

3.  Portions of walls with openings shall not be considered part of the shear wall length.

4. Required shearwall lengths perpendicular to the ridge are per lineal foot of building length. Multiply tabular values by building length for total shear wall length.

5. Shearwall lengths for no. 4 reinforcement are based on shearwall segment height of 80 inches and shearwall segment length of 24 inches. Multiply tabular length by shearwall adjustment factor from Table R609.5.1S for other segment lengths and heights.

6. Shearwall lengths for no. 5 reinforcement are based on shearwall segment height of 96 inches and shearwall segment length of 24 inches. Multiply tabular length by shearwall adjustment factor from Table R609.5.1S for other segment height lengths and heights.

Table R609.5.1Q Grade 40, revise text to read as follows:

| TABLE R609.5.1Q GRADE 40 REQUIRED SHEARWALL LENGTH PERPENDICULAR TO RIDGE NO. 4 REINFORCEMENT PER FOOT OF BUILDING LENGTH1,2,3,4,5 |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ROOF ANGLE 450 |  |  |  |  |  |  |  |  |  |  |
|  |  | TOP STORY |  |  | 1ST STORY OF 2 STORY OR 2ND STORY OF 3 STORY |  |  | 1ST STORY OF 3 STORY |  |  |
| Exp | Wind Speed | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  |
|  |  | 24 | 32 | 40 | 24 | 32 | 40 | 24 | 32 | 40 |
| B | 100 | 0.170 | 0.204 | 0.242 | 0.281 | 0.316 | 0.353 | 0.392 | 0.427 | 0.464 |
|  | 110 | 0.205 | 0.247 | 0.292 | 0.340 | 0.382 | 0.427 | 0.475 | 0.517 | 0.562 |
|  | 120 | 0.244 | 0.294 | 0.348 | 0.405 | 0.455 | 0.508 | 0.565 | 0.615 | 0.669 |
|  | 130 | 0.287 | 0.345 | 0.408 | 0.475 | 0.534 | 0.597 | 0.663 | 0.722 | 0.785 |
|  | 140 | 0.333 | 0.401 | 0.474 | 0.551 | 0.619 | 0.692 | 0.769 | 0.837 | 0.910 |
|  | 150 | 0.382 | 0.460 | 0.544 | 0.632 | 0.710 | 0.794 | 0.883 | 0.961 | 1.045 |
| C | 100 | 0.238 | 0.287 | 0.339 | 0.394 | 0.443 | 0.495 | 0.550 | 0.599 | 0.651 |
|  | 110 | 0.288 | 0.347 | 0.410 | 0.477 | 0.536 | 0.599 | 0.666 | 0.725 | 0.788 |
|  | 120 | 0.343 | 0.413 | 0.488 | 0.567 | 0.637 | 0.713 | 0.792 | 0.862 | 0.937 |
|  | 130 | 0.402 | 0.484 | 0.572 | 0.666 | 0.748 | 0.836 | 0.930 | 1.012 | 1.100 |
|  | 140 | 0.466 | 0.562 | 0.664 | 0.772 | 0.868 | 0.970 | 1.078 | 1.174 | 1.276 |
|  | 150 | 0.535 | 0.645 | 0.762 | 0.887 | 0.996 | 1.113 | 1.238 | 1.347 | 1.465 |

Notes:

1.  The cumulative shear wall segment length for each side of the building shall be equal to or greater than the tabular shear wall length required.  If the required shear wall segment length provided is not continuous the total shear wall length required shall be increased by 8" for each additional shear wall segment on a side.

2.  Minimum shear wall segment length shall be 2'-0". A grouted cell with reinforcing steel shall be provided at each end of every shear wall segment. A minimum length of 24 inches (610 mm) of solid wall segment, extending the full height of each wall, shall be provided at exterior corners of exterior walls. A fully grouted cell with reinforcing steel shall be provided at each end of every shear wall segment.

3.  Portions of walls with openings shall not be considered part of the shear wall length.

4. Required shearwall lengths perpendicular to the ridge are per lineal foot of building length. Multiply tabular values by building length for total shear wall length.

5. Shearwall lengths for no. 4 reinforcement are based on shearwall segment height of 80 inches and shearwall segment length of 24 inches. Multiply tabular length by shearwall adjustment factor from Table R609.5.1S for other segment lengths and heights.

6. Shearwall lengths for no. 5 reinforcement are based on shearwall segment height of 96 inches and shearwall segment length of 24 inches. Multiply tabular length by shearwall adjustment factor from Table R609.5.1S for other segment height lengths and heights.

Table R609.5.1R Grade 40, revise text to read as follows:

| TABLE R609.5.1R GRADE 40 REQUIRED SHEARWALL LENGTH PERPENDICULAR TO RIDGE NO. 5 REINFORCEMENT PER FOOT OF BUILDING LENGTH1,2,3,4,6 |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ROOF ANGLE 450 |  |  |  |  |  |  |  |  |  |  |
|  |  | TOP STORY |  |  | 1ST STORY OF 2 STORY OR 2ND STORY OF 3 STORY |  |  | 1ST STORY OF 3 STORY |  |  |
| Exp | Wind Speed | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  | BUILDING WIDTH |  |  |
|  |  | 24 | 32 | 40 | 24 | 32 | 40 | 24 | 32 | 40 |
| B | 100 | 0.116 | 0.140 | 0.165 | 0.192 | 0.216 | 0.241 | 0.268 | 0.292 | 0.317 |
|  | 110 | 0.140 | 0.169 | 0.200 | 0.232 | 0.261 | 0.292 | 0.324 | 0.353 | 0.384 |
|  | 120 | 0.167 | 0.201 | 0.237 | 0.276 | 0.310 | 0.347 | 0.386 | 0.420 | 0.456 |
|  | 130 | 0.196 | 0.236 | 0.279 | 0.324 | 0.364 | 0.407 | 0.453 | 0.493 | 0.536 |
|  | 140 | 0.227 | 0.273 | 0.323 | 0.376 | 0.422 | 0.472 | 0.525 | 0.572 | 0.621 |
|  | 150 | 0.261 | 0.314 | 0.371 | 0.432 | 0.485 | 0.542 | 0.603 | 0.656 | 0.713 |
| C | 100 | 0.162 | 0.196 | 0.231 | 0.269 | 0.302 | 0.338 | 0.376 | 0.409 | 0.444 |
|  | 110 | 0.196 | 0.237 | 0.280 | 0.325 | 0.366 | 0.409 | 0.454 | 0.495 | 0.538 |
|  | 120 | 0.234 | 0.282 | 0.333 | 0.387 | 0.435 | 0.486 | 0.541 | 0.589 | 0.640 |
|  | 130 | 0.274 | 0.331 | 0.391 | 0.455 | 0.511 | 0.571 | 0.635 | 0.691 | 0.751 |
|  | 140 | 0.318 | 0.383 | 0.453 | 0.527 | 0.592 | 0.662 | 0.736 | 0.801 | 0.871 |
|  | 150 | 0.365 | 0.440 | 0.520 | 0.605 | 0.680 | 0.760 | 0.845 | 0.920 | 1.000 |

Notes:

1.  The cumulative shear wall segment length for each side of the building shall be equal to or greater than the tabular shear wall length required.  If the required shear wall segment length provided is not continuous the total shear wall length required shall be increased by 8" for each additional shear wall segment on a side.

2.  Minimum shear wall segment length shall be 2'-0". A grouted cell with reinforcing steel shall be provided at each end of every shear wall segment. A minimum length of 24 inches (610 mm) of solid wall segment, extending the full height of each wall, shall be provided at exterior corners of exterior walls. A fully grouted cell with reinforcing steel shall be provided at each end of every shear wall segment.

3.  Portions of walls with openings shall not be considered part of the shear wall length.

4. Required shearwall lengths perpendicular to the ridge are per lineal foot of building length. Multiply tabular values by building length for total shear wall length.

5. Shearwall lengths for no. 4 reinforcement are based on shearwall segment height of 80 inches and shearwall segment length of 24 inches. Multiply tabular length by shearwall adjustment factor from Table R609.5.1S for other segment lengths and heights.

6. Shearwall lengths for no. 5 reinforcement are based on shearwall segment height of 96 inches and shearwall segment length of 24 inches. Multiply tabular length by shearwall adjustment factor from Table R609.5.1S for other segment height lengths and heights.

Table R609.5.1S Shearwall Length Adjustment Factor Grade 40 Steel, revise to read as follows [per the 2009 Supplement]:

Tables R609.5.3A and B, R609.5.4, R609.6.1.2 (1-3) R609.6.2.1(1 – 3), and R609.6.3.2(1 – 3)  Add from the 2007 FBC.

R611

EXTERIOR CONCRETE WALL CONSTRUCTION

R611.2 Applicability limits. The provisions of this section shall apply to the construction of exterior concrete walls for buildings not greater than 60 feet (18 288 mm) in plan dimensions, floors with clear spans not greater than 32 feet (9754 mm) and roofs with clear spans not greater than 40 feet (12 192 mm). Buildings shall not exceed 35 feet (10 668 mm) in mean roof height or two stories in height above-grade. Floor/ceiling dead loads shall not exceed 10 pounds per square foot (479 Pa), roof/ceiling dead loads shall not exceed 15 pounds per square foot (718 Pa) and attic live loads shall not exceed 20 pounds per square foot (958 Pa). Roof overhangs shall not exceed 2 feet (610 mm) of horizontal projection beyond the exterior wall and the dead load of the overhangs shall not exceed 8 pounds per square foot (383 Pa).

Walls constructed in accordance with the provisions of this section shall be limited to buildings subjected to a maximum design wind speed of 130 miles per hour (58 m/s) Exposure B, 110 miles per hour (49 m/s) Exposure C and 100 miles per hour (45 m/s) Exposure D. Walls constructed in accordance with the provisions of this section shall be limited to detached one- and two-family dwellings and townhouses assigned to Seismic Design Category A or B, and detached one- and two-family dwellings assigned to Seismic Design Category C.

Buildings that are not within the scope of this section shall be designed in accordance with PCA 100 or ACI 318.

Previous change to Section R611.7.1.2 is no longer needed. ICF walls have been integrated into the general wall category.  New TABLE R611.6(2) [or R611.6(4)], MINIMUM VERTICAL REINFORCEMENT FOR WAFFLE-GRID ABOVE-GRADE WALLS appears to be applicable. It is based on ASCE 7 but only goes up to 130 mph.  IRS ’09 Section R611.8.1.2, Vertical reinforcement, may be applicable; it has no apparent FL specific changes.

R611.7.1.2 Vertical steel. Above-grade concrete walls shall have reinforcement in accordance with Sections R611.3, R611.4, or R611.5 and R611.7.2. All vertical reinforcement in the top-most ICF story shall terminate with a 90-degree (1.57 rad) standard hook in accordance with Section R611.7.1.5. The free end of the hook shall be within 4 inches (102mm)of the top of the ICF wall and shall be oriented parallel to the horizontal steel in the top of the wall.

For townhouses in Seismic Design Category C, the minimum vertical reinforcement shall be one No. 5 bar at 24 inches (610mm)…..

Above-grade ICF walls …greater amount of reinforcement. [No change to paragraph]

Vertical reinforcement shall be …shall have a standard hook. [No change to paragraph]

Review for Florida Specific – Structural TAC

IRC ’09 Section R611.8 has been rewritten. The following tables have Florida-specific content that needs to be resolved.

TABLE R611.8(2)—continued

MAXIMUM ALLOWABLE CLEAR SPANS FOR 4-INCH NOMINAL THICK FLAT LINTELS IN LOAD-BEARING WALLSa, b, c, d, e, f, m

ROOF CLEAR SPAN 40 FEET AND FLOOR CLEAR SPAN 32 FEET

For SI: 1 inch = 25.4 mm; 1 foot = 304.8 mm; 1 pound per square foot = 0.0479kPa; Grade 40 = 280 MPa; Grade 60 = 420 MPa.

e. Reserved.

Staff recommendation:   Recommend limiting the scope of Table R611.8(2)to wind speed of 100 mph or less.  The IRC09 limits the use of IRC conventional construction requirements to 100 mph or less in hurricane-prone regions.

TABLE R611.8(3)

MAXIMUM ALLOWABLE CLEAR SPANS FOR 6-INCH NOMINAL THICK FLAT LINTELS IN LOAD-BEARING WALLSa, b, c, d, e, f, m

ROOF CLEAR SPAN 40 FEET AND FLOOR CLEAR SPAN 32 FEET

(Remove snow load)

For SI: 1 inch = 25.4 mm; 1 foot = 304.8 mm; 1 psf = 0.0479kPa; Grade 40 = 280 MPa; Grade 60 = 420 MPa.

e. Reserved.

TABLE R611.8(4)

MAXIMUM ALLOWABLE CLEAR SPANS FOR 8-INCH NOMINAL THICK FLAT LINTELS IN LOAD-BEARING WALLSa, b, c, d, e, f, m

ROOF CLEAR SPAN 40 FEET AND FLOOR CLEAR SPAN 32 FEET

(Remove snow load)

e. Reserved.

TABLE R611.8(5)

MAXIMUM ALLOWABLE CLEAR SPANS FOR 10-INCH NOMINAL THICK FLAT LINTELS IN LOAD-BEARING WALLSa, b, c, d, e, f, m

ROOF CLEAR SPAN 40 FEET AND FLOOR CLEAR SPAN 32 FEET

(Remove snow load)

e. Reserved.

TABLE R611.8(6)

MAXIMUM ALLOWABLE CLEAR SPANS FOR 6-INCH THICK WAFFLE-GRID LINTELS IN LOAD-BEARING WALLSa, b, c, d, e, f, o

MAXIMUM ROOF CLEAR SPAN 40 FEET AND MAXIMUM FLOOR SPAN 32 FEET

(Remove snow load)

e. Reserved.

TABLE R611.8(7)

MAXIMUM ALLOWABLE CLEAR SPANS FOR 8-INCH THICK WAFFLE-GRID LINTELS IN LOAD-BEARING WALLSa, b, c, d, e, f, o

MAXIMUM ROOF CLEAR SPAN 40 FEET AND MAXIMUM FLOOR CLEAR SPAN 32 FEET

(Remove snow load)

e. Reserved.

TABLE R611.8(8)

MAXIMUM ALLOWABLE CLEAR SPANS FOR 6-INCH THICK SCREEN-GRID LINTELS IN LOAD-BEARING WALLSa, b, c, d, e, f, p

ROOF CLEAR SPAN 40 FEET AND FLOOR CLEAR SPAN 32 FEET

(Remove snow load)

e. Reserved.

Review and determine applicability – Structural TAC

IRC Sec. 611.9, Requirements for connections, has been totally rewritten. It contains a lot of material on connecting walls to roofs, especially for wind loads up to 130 mph.

Staff recommendation:   Recommend limiting the scope of Section 611.9 to wind speed of 100 mph or less.  The IRC09 limits the use of IRC conventional construction requirements to 100 mph or less in hurricane-prone regions.

SECTION 612

EXTERIOR WINDOWS AND DOORS

Section R612.6 [was R613.3] Exterior windows and doors.  Change to read as shown.

Section R613.3.1.1 Testing and labeling of skylights revise text to read as follows:

R612.6 [was R613.3.1] Testing and labeling. Exterior windows and glass doors shall be tested by an approved independent testing laboratory, and shall be labeled to indicate compliance with the requirements of one of the following specifications:

ANSI/AAMA/NWWDA101/I.S.2 or ANSI/AAMA/WDMA 101/I.S.2/NAFS or

AAMA/WDMA/CSA 101/I.S.2/A440 or TAS 202 (HVHZ shall comply with TAS 202 utilizing

ASTM E 1300-98 or ASTM E 1300-04 02).

Exterior windows and sliding glass doors shall be labeled with a permanent label, marking, or etching providing traceability to the manufacturer and product. The following shall also be required either on a permanent label or on a temporary supplemental label applied by the

manufacturer: information identifying the manufacturer, the product model/series number,

positive and negative design pressure rating, product maximum size, glazing thickness, impact resistance. Approval number, applicable test standard(s), and approved product certification agency, testing laboratory, evaluation entity or Miami-Dade Product Approval.

The labels are limited to one design pressure rating per reference standard. The temporary

supplemental label shall remain on the window or door until final approval by the building official.

Exceptions:

      - Door assemblies installed in nonhabitable areas where the door assembly and area are designed to accept water infiltration need not be tested for water infiltration.

      - Door assemblies installed where the overhang (OH) ration is equal to or more than 1 need not be tested for water infiltration. The overhang ratio shall be calculated by the following equation:

OH ratio = OH length/OH height

Where:

OH length = The horizontal measure of how far an overhang over a door projects out from door’s surface.

OH height = The measure of the distance from the door’s sill to the bottom of the overhang over a door.

      - Pass-through windows for serving from a single-famiily kitchen where protected by a roof overhang of 5 feet (1.5 m) or more shall be exempted from the requirements of the water infiltration test.

      - Decorative glazed openings.

Glass Strength: Products tested and labeled as conforming to ANSI/AAMA/NWWDA 101/I.S.2 or ANSI/AAMA/WDMA 101/I.S.2/NAFS or AAMA/WDMA/CSA 101/I.S.2/A440 or TAS 202 shall not be subject to the requirements of the Florida Building Code, Building. Determination of load resistance of glass for specific loads of products not tested and certified in accordance with SectionR612.6 [was R613.3.1] shall be designed to comply with ASTM E 1300. The temporary supplemental label shall designate the type and thickness of glass or glazing material.

Section R612.6.1 Comparative analysis.  Change text to read as follows:

R612.6.1 [was FL 613.3.2] Comparative Analysis Label. A temporary supplemental label conforming to AAMA 203, Procedural Guide for the Window Inspection and Notification System, shall be acceptable for establishing and communicating the calculated allowable design pressures higher than indicated on the label required by Section R613.3.1 for window or door sizes smaller than that required by the ANSI/AAMA/NWWDA 101/I.S.2 or ANSI/AAMA/WDMA 101/I.S.2/NAFS or AAMA/WDMA/CSA 101/I.S.2/A440 test requirements. This temporary supplemental label shall be applied by the manufacturer and remain on the window or door until final approval by the building official.

R612.8 [was R613.4] Exterior door assemblies. Exterior door assemblies not covered by Sections R612.6 [was R613.3] or R612.8.3 [was R613.4.3] shall comply with Sections R612.8.1 [was R613.4.1] or R612.8.2  [was R613.4.2].

R612.8.1 [was R613.4.1] Exterior door assemblies shall be tested for structural integrity in accordance with ASTM E 330 Procedure A at a load of 1.5 times the required design pressure load. The load shall be sustained for 10 seconds with no permanent deformation of any main frame or panel member in excess of 0.4 percent of its span after the load is removed. HVHZ shall comply with TAS 202. After each specified loading, there shall be no glass breakage, permanent damage to fasteners, hardware parts, or any other damage which causes the door to be inoperable.

The minimum test sizes and minimum design pressures shall be as indicated in Table R613.4

The unit size tested shall qualify all units smaller in width and/or height of the same operation type and be limited to cases where frame, panels and structural members maintain the same profile as tested.

R612.8.2 [was R613.4.2]  Sectional garage doors shall be tested for determination of structural performance under uniform static air pressure difference in accordance with ANSI/DASMA 108 or TAS 202 (HVHZ shall comply with TAS 202).

R612.8.3 [was R613.4.3] Custom doors. Custom (one of a kind) exterior door assemblies shall be tested by an approved testing laboratory or be engineered in accordance with accepted engineering practices.

R612.8.4 [was R613.4.4]  Door components evaluated by an approved product evaluation entity, certification agency, testing laboratory or engineer may be interchangeable in exterior door assemblies provided that the door component( s) provide equal or greater structural performance as demonstrated by accepted engineering practices.

R612.8.4.1 [was R613.4.4.1] Optional exterior door component testing. With the exception of HVHZ, exterior side-hinged door assemblies not covered by Section R612.6 [was R613.3] shall have the option to have the components of the assembly tested and rated for structural integrity in accordance with the following specification:

SDI A250.13

Following the structural testing of exterior door components, there shall be no permanent deformation of any perimeter frame or panel member in excess of 0.4 percent of its span after the load is removed. After each specified loading, there shall be no glass breakage, permanent damage to fasteners, hardware parts, or any other damage that causes the door to be inoperable, as applicable.

R612.8.5 [was R613.4.5] Garage door labeling. Garage doors shall be labeled with a permanent label provided by the manufacturer. The label shall identify the manufacturer, the garage door model/series number, the positive and negative design pressure rating, indicate impact rated if applicable, the installation instruction drawing reference number, the Florida Product Approval or Miami-Dade Product Approval number if applicable, and the applicable test standards.

The required garage door components for an approved garage door assembly may be indicated using a checklist format on the label. If a checklist format is used on the label, the installer or manufacturer shall mark the selected components on the checklist that are required to assemble an approved garage door system.

The installation instructions shall be provided and available on the job site.

Section R612.8 Other exterior window and door assemblies.  Change to read as shown.

R612.8 Other exterior door assemblies. Exterior door assemblies not covered by Sections R612.6 [was R613.3] or R613.4.3 shall comply with Sections R613.4.1 or R613.4.2.

R612.9 Windborne debris protection.  Change to read as shown.

R612.9 [was 613.5] Windborne debris protection. Protection of exterior windows , glass doors and other glazed areas shall be in accordance with Section R 301.2.1.2.

R612.9.1 Fenestration testing and labeling. Reserved.

R612.10 [was 613.6] Anchorage methods.  Change to read as shown.

R612.10 Anchorage methods.

R612.10.1 Anchoring requirements. Window and door assembly anchoring systems shall be tested to achieve the design pressure specified. Substitute anchoring systems used for substrates not specified by the fenestration manufacturer shall provide equal or greater anchoring performance as demonstrated by accepted engineering practice. When provided, the manufacturer’s published installation instructions for as tested or substitute anchoring systems can be used. In no case shall the anchorage exceed the spacing for the tested rated performance.

R612.10.2 Anchorage details. Reserved.

R612.10.2.1 [was FL 613.6.1.1] Masonry, concrete or other structural substrate. Where the wood shim or buck thickness is less than 1 ½ inches (38 mm), window and door assemblies shall be anchored through the main frame or by jamb clip or subframe system, in accordance with the manufacturers published installation instructions. Anchors shall be securely fastened directly into the masonry, concrete or other structural substrate material. Unless otherwise tested, bucks shall extend beyond the interior face of the window or door frame such that full support of the frame is provided. Shims shall be made from materials capable of sustaining applicable loads, located and applied in a thickness capable of sustaining applicable loads. Anchors shall be provided to transfer load from the window or door frame to the rough opening substrate.

Where the wood buck thickness is 1 ½ inches (38 mm) or greater, the buck shall be securely fastened to transfer load to the masonry, concrete or other structural substrate and the buck shall extend beyond the interior face of the window or door frame. Window and door assemblies shall be anchored through the main frame or by jamb clip or subframe system or through the flange to the secured wood buck in accordance with the manufacturers published installation instructions. Unless otherwise tested, bucks shall extend beyond the interior face of the window or door frame such that full support of the frame is provided. Shims shall be made from materials capable of sustaining applicable loads, located and applied in a thickness capable of sustaining applicable loads. Anchors shall be provided to transfer load from the window or door frame assembly to the secured wood buck.

R612.10.2.2 [was FL 613.6.1.2] Wood or other approved framing material. Where the framing material is wood or other approved framing material, window and glass door assemblies shall be anchored through the main frame or by jamb clip or subframe system or through the flange in accordance with the manufacturer’s published installation instructions. Shims shall be made from materials capable of sustaining applicable loads, located and applied in a thickness capable of sustaining applicable loads. Anchors shall be provided to transfer load from the window or door frame to the rough opening substrate.

R612.11  [was 613.7.1] Mullions.

R612.11  Mullions.  Mullions, other than mullions which are an integral part of a window or glass door assembly tested and labeled in accordance with Section R613.3.1, shall be tested by an approved testing laboratory in accordance with AAMA 450 or be engineered in accordance with accepted engineering practice and shall meet the following criteria:

1. [was 613.7.1.1] Engineered mullions. Mullions qualified by accepted engineering practice shall comply with the performance criteria in Sections R612.11.2, R612.11.2, and R612.11.3.

2. [was FL613.7.1.2] Mullions tested as stand alone units. Mullions tested as stand alone units in accordance with AAMA 450 shall comply with the performance criteria in Sections R612.11.2, R612.11.2, and R612.11.3.

3. [was FL613.7.1.3] Mullions tested in an assembly. Mullions qualified by a test of an entire assembly in accordance with AAMA 450 shall comply with Sections R612.11.1 and R612.11.3.

R612.11.1  [was FL613.7.2] Load transfer.  Mullions shall be designed to transfer the design pressure loads applied by the window and door assemblies to the rough opening substrate.

R612.11.2 [was FL613.7.3] Deflection.  Mullions shall be capable of resisting the design pressure loads applied by the window and door assemblies to be supported without deflecting more than L/175, where L is the span of the mullion in inches.

R612.11.3 [was FL613.7.4] Structural safety factor.  Mullions shall be capable of resisting a load of 1.5 times the design pressure loads applied by the window and door assemblies to be supported without exceeding the appropriate material stress levels. If tested by an approved laboratory, the 1.5 times the design pressure load shall be sustained for 10 seconds, and the permanent deformation shall not exceed 0.4 percent of the mullion span after the 1.5 times design pressure load is removed.

Section R612.11.4 [was FL613.7.5]. Add to read as shown.

R612.11.4 [was FL613.7.5] Installation instructions for exterior windows and doors.  Windows and doors shall be installed in accordance with ASTM E 2112 or in accordance with the manufacturer’s installation instruction.

Section R612.12 [was FL613.8.1]. Add text to read as follows:

R612.12 Flashing, sealants and weatherstripping. Flashing and sealants for exterior windows and doors shall comply with Section R703.8.

R612.12.1 [was FL613.8.1] All exterior fenestration products shall be sealed at the juncture with the building wall with a sealant complying with AAMA 800 or ASTM C 920 Class 25 Grade NS or greater for proper joint expansion and contraction, ASTM C 1281, AAMA 812, or other approved standard as appropriate for the type of sealant.

R612.12.2 [was FL613.8.2] Masonry rough openings. Masonry rough opening dimensions shall be within the tolerances specified at Section R606.16 and in addition shall provide for a window perimeter sealant joint a maximum of 1/4 inches in width.

SECTION R613

STRUCTURAL INSULATED PANEL WALL CONSTRUCTION

SECTION R614

COMBINED CONCRETE, MASONRY, OR ICF AND WOOD EXTERIOR WALL CONSTRUCTION

R614.1 General. This section prescribes construction requirements for individual building elements where one or more exterior walls above the foundation contain multiple construction types. Where specific construction requirements are not specifically prescribed in this section, the requirements in the applicable sections of each material shall govern.

R614.2 Concrete, masonry, or ICF first story, wood frame second and third story.

R614.2.1 Foundation. The foundation system shall be designed in accordance with Chapter 4.

R614.2.2 First-story construction. The concrete, masonry or ICF first-story shall be in accordance with Chapter 6 for the applicable first-story construction method.

R614.2.3 Floor systems. The second- and third-story floor system shall be in accordance with Chapter 5.

R614.2.4 Second- and third-story construction. The second- and third-story walls, ceilings and roof shall be in accordance with the appropriate sections in Chapters 6, 8 and 9.

R614.2.5 Shear wall connections. Second- story shearwalls shall be connected to first-story walls in accordance with Tables 3.2A, 3.2B, 3.2C, A-3.2A, A-3.2B or A-3.2C of the AF&PA Wood Frame Construction Manual for One- and Two-Family Dwellings as applicable.

R614.3 Wood frame gable endwalls above concrete, masonry, or ICF walls. This condition is not permitted unless there is a ceiling diaphragm in accordance with Figures 3.7a and 3.15 of the AF&PA Wood Frame Construction Manual for One- and Two-Family Dwellings.

R614.3.1 Gable construction. Gable construction shall be in accordance with the AF&PA Wood Frame Construction Manual for One- and Two-Family Dwellings.

R614.3.2 Wall construction. Concrete, masonry or ICF wall construction shall be in accordance with Chapter 6.

R614.3.3 Gable connection. The connection of the wood frame gable endwall to the concrete, masonry or ICF wall shall be in accordance with Figures R614.3(1) and R614.3(2), or Figure R609.4.

Section R615 add new section to read as shown:

SECTION R615

IMPACT-RESISTANT COVERINGS

R615 Impact resistant coverings.

R615.1 Impact resistant coverings shall be tested at 1.5 times the design pressure (positive or negative) expressed in pounds per square feet as determined by the Florida Building Code, Building Section 1609 for which the specimen is to be tested.

R615.1.1 Impact resistant coverings shall be labeled in accordance with the provisions of Section 1714.8.

R615.2. Labels. A permanent label shall be provided by the product approval holder on all impact resistant coverings.

R615.2.1  The following information shall be included on the labels on impact resistant coverings:

- Product approval holder name and address.

- All applicable methods of approval. Methods of approval include, but, are not limited to Miami-Dade NOA; Florida Building Commission, TDI Product Evaluation; ICC-ES.

- The test standard or standards specified at Section 1609.1.4, including standards referenced within the test standards specified at Section 1609.1.4 used to demonstrate code compliance.

- For products with a Florida Product Approval Number or a Miami-Dade County Building Code Compliance Office Notice of Acceptance Number (NOA), such numbers shall be included on the label.

R615.3 Location of label. The location of the label on the impact resistant covering shall be as follows:

- Accordions: Bottom of the locking bar or center mate facing the exterior or outside.

- Rollup: On the bottom of the hood facing the exterior or outside or on the bottom slat facing the exterior or outside.

- Bahama Awning or Colonial Hinged: On the bottom, placed on the back of the shutter.

- Panels: For metal and plastic panels the label may be embossed or printed spaced not more than every three (3) lineal feet on each panel. The label shall be applied by the holder of the product approval and shall face the exterior or outside.

- Framed products: The label shall be on the side or bottom facing the exterior or outside.

- Labels on all other products shall face the exterior or outside.

R615.4 Installation. All impact resistant coverings shall be installed in accordance with the manufacturer’s installation instructions and in accordance with the product approval. Installation instructions shall be provided and shall be available to inspection personnel on the job site. Opening protection components, fasteners, and other parts evaluated by an approved product evaluation entity, certification agency, testing laboratory, architect, or engineer and approved by the holder of the product approval may be interchangeable in opening protection assemblies provided that the opening protection component(s) provide equal or greater structural performance and durability as demonstrated by testing in accordance with approved test standards.

Section R616 Prescriptive requirements for window installation in wood frame construction.  Add to read as shown.

SECTION R616

PRESCRIPTIVE REQUIREMENTS FOR WINDOW INSTALLATION

IN WOOD FRAME CONSTRUCTION

R616.1 General

R616.1.1 The provisions of this section shall cover the installation of windows in buildings utilizing a membrane/drainage system of not more than 3 stories in height.

R616.1.2 The provisions of this section apply to windows which employ a mounting flange or fin that is attached and sealed to the window perimeter frame and is designed as an installation fastening appendage.

R616.1.3 The provisions of this section cover the installation process for the described windows and do not include fabrication techniques that would be required to join individual windows to each other, either horizontally or vertically. It does not cover any other factory or field fabrication which joins or combines multiple windows. The instructions for mulling windows together and any accessories required must be supplied by the window manufacturer.

R616.1.4 The provisions of this section provide minimum requirements for window installation, based on current best practices. Actual conditions in buildings may vary. In cases where variations occur the installer shall consult with the window manufacturer or registered design professional. If the provisions of this section conflicts with the manufacturer’s instruction, the manufacturer’s instruction shall take precedence.

R616.2 Water resistance.

R616.2.1 Water-Resistive Barriers (WRB) The installation of the WRB shall be installed prior to the window installation. The application of the WRB involves covering the vertical surfaces of the wall, lapped, fastened, taped, and sealed per the WRB manufacturer’s instructions.  Penetrations through the WRB for the installation of windows shall be made pursuant to this standard by the window installer. Apply the WRB in water shedding fashion, starting at the base of the wall and working towards the top. Install the water-resistive barrier (WRB) to the face of the building framing or sheathing.

R616.2.2 Sealants  All gunable sealants shall comply with AAMA 808.5 (per AAMA 800) and ASTM C 920 Class 25 Grade NS or greater for proper joint expansion and contraction. If preformed tapes are used they shall meet ASTM C1281 specification. Prior to using the sealants the applicator shall seek input from sealant manufacturer for proper joint design, material compatibility, and sealant selection.  Aerosol foam sealants shall perform to the AAMA 812 standard.

R616.2.3 Cladding Application Stucco and other cladding shall not be installed prior to window installation.

R616.2.4 Pre-Installation

R616.2.4.1 Pre-Installation Inspection. Prior to the installation of the window an inspection of the WRB shall be made by the window installer to ensure that it has been installed in accordance with the WRB manufacturer’s instructions.  Any tears, penetrations, or defects within 12 inches past the rough opening area shall be sealed per the WRB manufacturer’s instructions before the installation starts.  Refer to ASTM C 755.

R616.3   Window Installation Procedures

R616.3.1  Installation Procedures

R616.3.1.1 In the event that the WRB has not been modified the installer shall complete the following steps. Carefully cut the WRB in a modified “I” pattern per ASTM E2112.  A full “I” cut is also acceptable.  Fold the bottom and side flaps over and behind the interior side of the framing. Attach the WRB into position on the inside of the rough opening, and trim any excess as required.

R616.3.1.2 At the head of the opening, starting at the top corner of the window (rough) opening, measure from the corner horizontal and then vertical a dimension equal to the roll width of the flashing to be applied, and make a mark. At a 45° angle, carefully cut the WRB on a diagonal. Repeat this step on the opposite corner. Gently raise the bottom edge of the flap created in the WRB up and temporarily tape the top corners and center to the exterior face of the WRB above. This is done in order to allow for installation of the window and head flashing later.

R616.3.2 Apply horizontal sill flashing material.  If a rigid or semi-rigid sill pan system is used, apply sill flashing level with the top edge of the rough opening sill.

R616.3.2.1 Self-adhering flashing (SAF) is able to serve as both horizontal sill flashing and the sill pan with sufficient width. The self-adhered flashing must cover the sill to at least the depth of the window plus 2 inches onto the face of the WRB drainage plane. Cut the sill flashing long enough to extend an equal distance beyond the rough opening width. Cut a length equal to the rough opening width plus two times the roll width of the jamb flashing.  When mechanical flashing is used the minimum roll width shall be 9 inches, while self adhering flashing shall be a minimum of 4 inches.

R616.3.3 Install a rigid or semi-rigid sill pan system. The pan shall direct water to the exterior or to the membrane drainage plane for subsequent drainage to the exterior of the building. When the sill pan is made of metal and includes end dams, seal the sill pan into position, integrating the end dams with the WRB and the down turned leg of the sill pan with the flashing. Self-adhering flashing may also be used to seal the end dam to the WRB at the jamb condition.

R616.3.4 Inspect and clean the back side (interior surface) of the exterior window mounting flange.  Look for any missing seals at the corner joinery.  If corner seals are missing or need to be touched up, contact the window manufacturer for the recommended type of sealant to apply and then reapply as necessary.

R616.3.5 Apply a continuous 3/8-inch nominal diameter bead of sealant to the back surface (interior face) of the mounting flange of the window at the head and both jambs. Apply sealant in line with any pre-punched holes or slots in the mounting flange. Connect that bead of sealant across any joinery on the window frame at all four corners.   At an option, the sealant shall be permitted to be applied to the wall surface as opposed to the back of the mounting flange.

R616.3.6 Apply a discontinuous bead of sealant on the interior surface of the mounting flange at the sill.  The bead of sealant is to have a minimum of (2) 2 inch voids near the ends, which will allow any liquid water that has entered the window opening to exit easily.

R616.3.6.1 As an alternate to the discontinuous bead of sealant, a weep screed or wicking mechanism may be applied at the jamb ends of the sill to allow liquid water to escape.

R616.3.6.2 Additionally, if a rigid or semi-rigid sill pan is used, apply a bead of sealant to the outboard side of the upturned leg of the pan where it will integrate with the interior side of the window and form an air/water seal.

R616.3.7 Immediately set the window into the opening. Hold the window temporarily into position and apply shims as required to ensure the window is set plumb, level, square and true. Fasten the window perimeter securely into position in accordance with the manufacturer’s instructions.  Install shims in such a manner that they will not interfere with the application of the air seal; which will be applied on the interior side in the steps that follow.

R616.3.8 Flashing shall be applies over the mounting flange of the window at both jambs.  Either self-adhesive flashing or mechanical flashing shall be permitted to be used in the following steps.  When self-adhering flashing is used, the additional bead of sealant over the mounting flange (see R616.3.8.2) shall be omitted.

R616.3.8.1 Cut the flashing to a measurement equal to twice the roll width of the flashing being used, plus the height of the rough opening, minus 1 inch.

R616.3.8.2 When mechanical flashing is used, apply a continuous 3/8-inch nominal diameter bead of sealant over the wall and the exterior face of the mounting flange, starting 8 1/2 inches above the rough opening continuing down the jambs to the bottom of the sill mounting flange.  Apply in line with any pre-punched holes/slots in the mounting flange and cover any fastener heads.

R616.3.8.3 Position the top end of the flashing ½-inch below where the top edge of the head flashing will cover the jamb flashing later.  Do not interfere with the WRB flap at the head. Tuck the top of the jamb flashing under the flap of the water-resistive barrier at the head.

R616.3.9 Apply a piece of flashing across the head of the rough opening. Either self-adhering flashing or mechanical flashing may be used.  Where self-adhering flashing is used, the sealant over the mounting flange (see R616.3.9.3) shall be omitted.

R616.3.9.1 Cut a piece of head flashing that is the width of the rough opening plus two times the roll width of the flashing plus 2 inches.

R616.3.9.2 Apply primer to any exposed OSB as required by the flashing manufacturer.

R616.3.9.3 When using mechanically applied flashing, apply a continuous 3/8-inch nominal diameter bead of sealant along the mounting flange at the head.  Apply the sealant in line with any pre-punched holes or slots in the mounting flange and cover any fastener heads.

R616.3.9.4 Adhere the flashing across the head of the window on top of the mounting flange and beyond the rough opening on each side extending it 1 inch over the outside edge of the flashing at the jambs. Fasten the mechanically applied flashing as needed.

R616.3.10 Remove the previously applied tape which holds the flap of the water-resistive barrier at the head. Allow the flap to lay flat over the head flashing.   Apply a new piece of sheathing tape over the entire diagonal cut made in the water-resistive barrier. The tape should be compressed against the WRB and the head flashing, which extends over the jamb.

R616.3.11 On the interior, the installer shall apply a backer rod and an interior perimeter bead of sealant or other window manufacturer approved material between the window and the rough opening on all sides to form an air seal. If a rigid or semi-rigid sill pan was used, recheck the seal between the sill of the window and the upturned leg of the sill pan and reseal as needed.

R616.3.11.1 In cases where shims cause interference with the application of the backer rod or sealant, trim excess shim material to allow for a continuous air/water seal. In all cases make sure the entire perimeter joint has been sealed, creating an air/water tight condition.

R616.4 Post Installation Procedure Drainage holes shall be inspected for blockage and freed of any obstructions to allow drainage.

CHAPTER 7 WALL COVERING

Add exception to R701.1 as follows:

R701.1 Application. The provisions of this chapter shall control the design and construction of the interior and exterior wall covering for all buildings.

Exception: Buildings and structures located within the High-Velocity Hurricane Zone shall comply with the provisions of Chapter 44.

R702.3.4 Insulating concrete form walls.  Change to read as shown.

R702.3.4 Insulating concrete form walls. Foam plastics for insulating concrete form walls constructed in accordance with Sections R404.1.2 and R611 on the interior of habitable spaces shall be protected  in accordance with Section R316.4 Adhesives are permitted to be used in conjunction with mechanical fasteners. Adhesives used for interior and exterior finishes shall be compatible with the insulating form materials.

Change referenced table in R702.3.5 as shown:

R702.3.5 Application. Maximum spacing of supports and the size and spacing of fasteners used to attach gypsum board shall comply with Table R702.3.5. Gypsum sheathing shall be attached to exterior walls in accordance with Table R602.2(1). [rest of section unchanged]

Change Section R703.1 as shown:

R703.1 General.  Exterior walls shall provide the building with a weather-resistant exterior wall envelope. The exterior wall envelope shall include flashing as described in Section R703.8.

All exterior finishes shall be applied in accordance with the manufacturer’s specifications or installation instructions.

.

Add subsection to R703.1 as shown:

R703.1.1.1  Load resistance. All exterior walls, wall coverings and soffits shall be capable  of resisting the design pressures specified in Table R301.2(2) for walls.

Delete Exception 3 to R703.2 as shown:

R703.2 Weather-resistant sheathing paper.  [Title and exceptions only FL specific]

Exceptions:

1 – 2.  [No change]

3.  Under paperbacked stucco lath when the paper backing is an approved weather-resistive sheathing paper.

Add subsections to R703.3 as shown:

R703.3.3 Attachment.  Wood, hardboard and wood structural panel siding shall be attached in accordance wit h Tables R703.3.3(1) and R703.3.3(2).  Specific gravities, G for solid sawn lumber are specified in Table 703.3.3(3).

R703.3.4 Minimum thickness.  Wood, hardboard and wood structural panel siding shall be of the minimum thickness specified in Tables R 703.3.4(1) and R703.3.4(2).

Add Tables to Section R703.3.3 as shown [see 2007 FBC, R]:

TABLE R703.3.3(1)  WOOD, HARDBOARD, AND WOOD STRUCTURAL PANEL SIDING ATTACHMENT EXPOSURE CATEGORY B

TABLE R703.3.3(2) WOOD, HARDBOARD, AND WOOD STRUCTURAL PANEL SIDING ATTACHMENT EXPOSURE CATEGORY C

TABLE R703.3.3(3) SPECIFIC GRAVITIES OF SOLID SAWN LUMBER

Add Tables to Section R703.3.4 as shown[see 2007 FBC, R]:

TABLE R703.3.4(1) WOOD, HARDBOARD, AND WOOD STRUCTURAL PANEL SIDING MINIMUM THICKNESS, EXPOSURE CATEGORY B

TABLE R703.3.4(2) WOOD, HARDBOARD, AND WOOD STRUCTURAL PANEL SIDING MINIMUM THICKNESS, EXPOSURE CATEGORY C

Use FL specific section R703.4 as shown:

R703.4 Attachments. Unless specified otherwise, all wall coverings shall be secured with approved aluminum, stainless steel, zinc-coated or other approved corrosion-resistive fasteners in accordance with the approved manufacturer’s installation instructions.  Where wind pressures determined in accordance with Table R301.2(2) do not exceed 30 psf, wall coverings are permitted to be installed in accordance with Table R703.4.

Table R703.4, change to read as follows:

TABLE R703.4

WEATHER-RESISTANT SIDING ATTACHMENT AND MINIMUM THICKNESS

TABLE R703.4

WEATHER–RESISTANT SIDING ATTACHMENT AND MINIMUM THICKNESS

| Siding Material |  | Nominal Thicknessa (inches) | Joint Treatment | Water-Resistive Barrier Required | Type of Supports for the Siding Material and Fastenersb,d |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | Wood or Wood Structural Panel Sheathing | Fiberboard Sheathing into Stud | Gypsum Sheathing into Stud | Foam Plastic Sheathing into Stud | Direct to Studs | Number or Spacing of Fasterners |  |  |  |  |
| NO change |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Hardboardk Panel siding-vertical |  | See Section R703.3.4 | – | Yes | See Section R703.3.4 |  |  |  |  |  |  |  |  | With Insulation |
| Hardboardk Lap-siding-horizontal |  | See Section R703.3.4 | Note q | Yes | See Section R703.3.4 |  |  |  |  |  |  |  |  |  |
| Steelh |  | 29 ga. | Lap | Yes | 0.113 nail 1 ¾” Staple-1 ¾” | 0.113 nail 2 ¾” Staple-2 1/2 ” | 0.113 nail 2 1/2” Staple-2 1/4” | 0.113 naily Stapley | Not allowed | Same as stud spacing |  |  |  |  |
| Stone veneer |  | 2 | Section R703 | Yes (Note 1) | See Section R703 and Figure R703.7c |  |  |  |  |  |  |  |  |  |
| Particleboard panels |  | 3/8-1/2 | – | Yes | 6d box nail (2” x 0.099”) | 6d box nail (2” x 0.099”) | 6d box nail (2” x 0.099”) | box nail | 6d box nail (2” x 0.099”) 3/8 not allowed | 6” panel edges 12” inter. Sup.o |  |  |  |  |
|  |  | 5/8 | – | Yes | 6d box nail (2” x 0.099”) | 8d box nail (2 1/2” x 0.113”) | 8d box nail (2 1/2” x 0.113”) | box nail | 6d box nail (2” x 0.099”) |  |  |  |  |  |
| No change |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Vinyl sidingm |  | 0.035 | Lap | Yes | See Section R703.3.4 |  |  |  |  |  |  |  |  |  |
| Woodj rustic, drop |  | 3/8 Min | Lap | Yes | Fastener penetration into stud-1” |  |  |  | 0.113 nail -2 1/2” Staple-2” | Face nailing up to 6” widths, 1 nail per bearing; 8” widths and over, 2 nails per bearing |  |  |  |  |
| Shiplap |  | 19/32 Average | Lap | Yes |  |  |  |  |  |  |  |  |  |  |
| Bevel |  | 7/16 |  |  |  |  |  |  |  |  |  |  |  |  |
| Butt tip |  | 3/16 | Lap | Yes |  |  |  |  |  |  |  |  |  |  |
| Fiber cement panel sidingr |  | No change | No change | No change | No change | No change | No change | No change | No change | No change |  |  |  |  |
| Fiber cement lap sidingr |  | No change | No change | No change | No change | No change | No change | No change | 6d corrosion-resistant nailw | Note w |  |  |  |  |

No change to the remaining text of the table.

For SI: 1 inch = 25.4 mm.

a-b no change

c. Reserved.

d-i no change.

m. Reserved.

n.  no change

o.  Reserved.

P – z  no change .

Change R703.5.3 as shown:

R703.5.3 Attachment.  Wood shakes and shingles, and attachment and supports shall be capable of resisting the wind pressures determined in accordance with Table R310.2(2). Where wind pressures determined in accordance with Table R301.2(2) do not exceed 30 psf, each shake or shingle shall be held in place by two hot-dipped zinc-coated, stainless steel, or aluminum nails. The fasteners shall be long enough to penetrate the sheathing or furring strips by a minimum of 1/2 inch (12.7 mm) and shall not be overdriven.  Where pressures determined in accordance with Table R301.2(2) exceed 30 psf, the attachment shall be designed to resist the prescribed wind pressures.

R703.5.3.1 Staple attachment. Reserved.

R703.6 Exterior plaster.

R703.6.1 Exterior use of Portland cement plaster shall comply with the application requirements of ASTM C 926. .

R703.6.2 Installation of exterior lathing and framing shall comply with the application requirements of ASTM C 1063.

Overlap with Florida Specific - Structural TAC

R703.6.3 as shown: Need to be resolved

FBC

R703.6.3 Where cement plaster (stucco) is to be applied to lath over frame construction, measures shall be taken to prevent bonding between the cement plaster and the water-resistive barrier. A bond break shall be provided between the water-resistive barrier and the cement plaster (stucco) consisting of one of the following:

1. Two layers of an approved water-resistant barrier material; or

2. One layer of an approved water-resistant barrier over an approved plastic house wrap; or

3. Other approved methods or materials applied in accordance with the manufacturer’s installation instructions.

R703.6.4 Pneumatically placed portland cement plaster.

R703.6.4.1 Pneumatically placed portland cement plaster shall be a mixture of portland cement and aggregate conveyed by air through a pipe or flexible tube, and deposited by air pressure in its final position.

R703.6.4.2 Rebound material may be screened and reused as aggregate in an amount not greater than 25 percent of the total sand in any batch.

R703.6.4.3 Pneumatically placed portland cement plaster shall consist of a mixture of one part cement to not more than five parts of aggregate. Plasticity agents may be used as specified elsewhere in this chapter. Except when applied to concrete or masonry, such plaster shall be applied in not less than two coats to a minimum total thickness of 7/8 inch (22.2 mm)

2009 IRC

R703.6.4 Application. Each coat shall be kept in a moist condition for at least 48 hours prior to application of the next coat.

Exception: Applications installed in accordance with ASTM C 926.

R703.6.5 Curing. The finish coat for two-coat cement plaster shall not be applied sooner than seven days after application of the first coat. For three-coat cement plaster, the second coat shall not be applied sooner than 48 hours after application of the first coat. The finish coat for three-coat cement plaster shall not be applied sooner than seven days after application of the second coat.

Staff recommendation:   The IRC09 does not cover Florida specific provisions. Recommend retaining Florida specific provisions as stated above.

Section R703.6.5 Fenestration.  Add new section to read as shown.

- R703.6.75 Fenestration.  The juncture of exterior plaster and fenestration products shall be sealed with a sealant complying with Section R613.8.1.

Overlap with Florida Specific – Structural TAC

FBC

Change R703.7 as shown: Need to be resolved

R703.7 Stone and masonry veneer, general. All stone and masonry veneer shall be installed in accordance with this chapter, Table R703.4 and Figure R703.7.  The provisions of this section are limited to areas where the wind speed is equal or less than 130 mph.

Exceptions: For detached one- and two- family dwellings, exterior masonry veneer with a backing of wood or cold-formed steel framing shall not exceed 30 feet (9144 mm) in height above the noncombustible foundation, with an additional 8 feet (2348 mm) permitted for gabled ends.

2009 IRC

R703.7 Stone and masonry veneer, general. Stone and masonry veneer shall be installed in accordance with this chapter, Table R703.4 and Figure R703.7. These veneers installed over a backing of wood or cold-formed steel shall be limited to the first story above-grade and shall not exceed 5 inches (127 mm) in thickness. See Section R602.12 for wall bracing requirements for masonry veneer for wood framed construction and Section R603.9.5 for wall bracing requirements for masonry veneer for cold-formed steel construction.

Exceptions:  Specific to Seismic

Staff recommendation:   The IRC09 does not cover Florida specific provisions. Recommend retaining Florida specific provisions as stated above.

TABLE R703.7(1)

STONE OR MASONRY VENEER LIMITATIONS AND REQUIREMENTS, WOOD

OR STEEL FRAMING, SEISMIC DESIGN CATEGORIES A, B AND C  Reserved.

TABLE R703.7(2)

STONE OR MASONRY VENEER LIMITATIONS AND REQUIREMENTS, ONE- AND TWO-FAMILY DETACHED DWELLINGS,

WOOD FRAMING, SEISMIC DESIGN CATEGORIES D0, D1 AND D2    Reserved.

Change R703.7.2 as shown:

R703.7.2 Exterior veneer support. Except in Seismic Design Categories D0, D1 and D2, Exterior masonry veneers having an installed weight of 40 pounds per square foot….[rest same as IRC]

Change the exception in R703.7.4.1 to read as shown:

R703.7.4.1 Size and spacing.  [No change to IRC text]

Exception:  Where the wind speed determined in accordance with Figure R301.2(4) exceeds 110 mph (176.99 km/h) or is less than or equal to 130 mph (208 km/h), each tie shall support not more than 1.8 square feet (0.167 m2) of wall area and anchors shall be spaced at a maximum 18 inches (457 mm) horizontally and vertically.

Change R703.7.4.2 to read as shown:

R703.7.4.2 Air space.  [No change to IRC text]

Exception:  Where the wind pressure determined in accordance with Table R301.2(2) exceeds 30 pounds per square foot pressure (1.44 kN/m2), the air space shall not exceed 2 inches (51 mm).

Change R703.9 as shown:

R703.9 Exterior insulation and finish system (EIFS)/EIFS with drainage. Exterior Insulation and Finish System (EIFS)  shall be designed or tested to meet the wind pressures specified in Table R301.2(2)   and shall comply with this chapter and Sections R703.9.1 and R703.9.3. EIFS with drainage shall comply with this chapter and Sections R703.9.2, R703.9.3 and R703.9.4.

No change to the rest of the section.

Overlap with Florida Specific -  Structural TAC

FBC

Change R703.10 as shown: Need to be resolved

R703.10 Fiber cement siding. Fiber-cement siding complying with ASTM C1186, Type A, minimum Grade II, shall be permitted on exterior walls in accordance with the approved manufacturer’s installation instructions.

R703.10.1  Fastening.  Fiber-cement siding shall be securely fastened with aluminum, copper, zinc, zinc-coated or other approved corrosion-resistant fasteners in accordance with the manufacturer’s approved  installation instructions.  Attachment and supports shall be capable of resisting the wind pressure determined in accordance with Table R301.2(2).  Where the wind pressure determined in accordance with Table R301.2(2) does not exceed 30 pounds per square foot pressure (1.44kN/m2), fiber-cement siding is permitted to be attached in accordance with Table R703.4.

R703.10.2  Panel Siding.  Panels shall be installed with the long dimension either parallel or perpendicular to framing.  Vertical and horizontal joints shall occur over framing members and shall be sealed with caulking or covered with battens.  Panel siding shall be installed with fasteners according to Table R703.4 or approved manufacturer’s installation instructions.

R703.10.3  Lap siding.  Lap siding having a maximum width of 12 inches shall be lapped a minimum of 1¼ inches (32 mm) and shall have the ends sealed with caulking, covered with an H-section joint cover, or located over a strip of flashing.  Lap siding courses may be installed with the fastener heads exposed or concealed, according to Table R703.4 or approved manufacturer’s installation instructions.

2009 IRC

R703.10 Fiber cement siding.

R703.10.1 Panel siding. Fiber-cement panels shall comply with the requirements of ASTM C1186, Type A, minimum Grade II. Panels shall be installed with the long dimension

either parallel or perpendicular to framing.Vertical and horizontal joints shall occur over framing members and shall be sealed with caulking, covered with battens or shall be designed to comply with Section R703.1. Panel siding shall be installed with fasteners according to Table R703.4 or

approved manufacturer’s installation instructions.

R703.10.2 Lap siding. Fiber-cement lap siding having a maximum width of 12 inches shall comply with the requirements of ASTM C1186, Type A, minimum Grade II. Lap siding shall be lapped a minimum of 11/4 inches (32 mm) and lap siding not having tongue-and-groove end joints shall have the ends sealed with caulking, installed with an H-section joint cover, located over a strip of flashing or shall be designed to comply with Section R703.1. Lap siding

courses may be installed with the fastener heads exposed or concealed, according to Table R703.4 or approved manufacturers’ installation instructions.

Staff recommendation:   The IRC09 does not cover Florida specific provisions. Recommend retaining Florida specific provisions as stated above.

Change R703.11 as shown:

R703.11 Vinyl Siding.  Vinyl siding shall comply with ASTM D 3679 and is permitted to be used on exterior walls in accordance with the manufacturer’s approved installation instructions.

R703.11.1 Labeling.  Vinyl Siding shall be labeled as conforming to the requirements of ASTM D 3679

Add new text R703.12 as shown:

R703.132 Metal veneers.  Veneers of metal shall be fabricated from approved corrosion-resistant materials or shall be protected front and back with porcelain enamel, or otherwise be treated to render the metal resistant to corrosion. Such veneers shall not be less than specified in Table R703.13 mounted on wood or metal furring strips or approved sheathing on the wood construction.

R703.132.1 Attachment. Exterior metal veneer shall be securely attached to the supporting masonry or framing members with corrosion-resistant fastenings, metal ties or by other approved devices or methods capable of resisting the wind pressures specified in Table R301.2(2)., but in no case less than 20 psf (0.958 kg/m2). Where the wind pressure determined in accordance with Table R301.2(2) do not exceed 30 pounds per square foot pressure (1.44 kN/m2), metal veneers are permitted to be attached in accordance with Table R703.4.

R703.132.2 Weather protection. Metal supports for exterior metal veneer shall be protected by painting, galvanizing or by other equivalent coating or treatment. Wood studs, furring strips or other wood supports for exterior metal veneer shall be approved pressure-treated wood or protected as required in Section 1403.2 of the Florida Building Code, Building. Joints and edges exposed to the weather shall be caulked with approved durable waterproofing material or by other approved means to prevent penetration of moisture.

R703.132.3 Aluminum Siding.  Aluminum siding shall conform to the requirements of AAMA 1402.

- R703.143 Weather protection. Exterior walls shall provide weather protection for the building. The materials of the minimum nominal thickness specified in Table R703.13 shall be acceptable as approved weather coverings.

| TABLE R703.143 |  |
| --- | --- |
| MINIMUM THICKNESS OF WEATHER COVERINGS |  |
| COVERING TYPE | MINIMUM THICKNESS |
|  | (inches) |
| Adhered masonry veneer | 0.25 |
| Anchored masonry veneer | 2.625 |
| Aluminum siding | 0.019 |
| Asbestos-cement boards | 0.125 |
| Asbestos shingles | 0.156 |
| Cold-rolled copperd | 0.0216 nominal |
| Copper shinglesd | 0.0162 nominal |
| Exterior plywood (with sheathing) | 0.313 |
| Exterior plywood (without sheathing) | See Section 2304.6 |
| Fiberboard siding | 0.5 |
| Fiber cement lap siding | 0.25c |
| Fiber cement panel siding | 0.25c |
| Glass-fiber reinforced concrete panels | 0.375 |
| Hardboard sidingc | 0.25 |
| High-yield copperd | 0.0162 nominal |
| Lead-coated copperd | 0.0216 nominal |
| Lead-coated high-yield copper | 0.0162 nominal |
| Marble slabs | 1 |
| Particleboard (with sheathing) | See Section 2304.6 |
| Particleboard (without sheathing) | See Section 2304.6 |
| Precast stone facing | 0.625 |
| Steel (approved corrosion resistant) | 0.0149 |
| Stone (cast artificial) | 1.5 |
| Stone (natural) | 2 |
| Structural glass | 0.344 |
| Stucco or exterior Portland cement plaster |  |
| Three-coat work over: |  |
| Metal plaster base | 0.875b nominal |
| Unit masonry | 0.625b nominal |
| Cast-in-place or precast concrete | 0.625b nominal |
| Two-coat work over: |  |
| Unit masonry | 0.5b nominal |
| Cast-in-place or precast concrete | 0.375b nominal |
| Terra cotta (anchored) | 1 |
| Terra cotta (adhered) | 0.25 |
| Vinyl siding | 0.035 |
| Wood shingles | 0.375 |
| Wood siding (without sheathing)a | 0.5 |
| For SI: 1 inch = 25.4 mm. |  |
| a. Wood siding of thicknesses less than 0.5 inch shall be placed over sheathing that conforms to Section 2304.6. |  |
| b. Exclusive of texture. |  |
| c. As measured at the bottom of decorative grooves. |  |
| d. 16 ounces per square foot for cold-rolled copper and lead-coated copper, 12 ounces per square foot for copper shingles, high-yield copper and ounces per square foot for copper shingles, high-yield copper and lead-coated high-yield copper. |  |

Add Section R703.14 as shown:

R703.154 Drained assembly wall over mass assembly wall.  Where wood frame or other types of drained wall assemblies are constructed above mass wall assemblies, flashing or other approved drainage system shall be installed as required by R703.8.

Add Section R704 as shown:

SECTION 704

INSPECTION FOR TERMITES

In order to provide for inspection for termite infestation, clearance between exterior wall coverings and final earth grade on the exterior of a building shall not be less than 6 inches (152 mm).

Exceptions:

1.	Paint or decorative cementitious finish less than 5/8 inch (17.1 mm) thick adhered directly to the masonry foundation sidewall.

2.	Access or vehicle ramps which rise to the interior finish floor elevation for the width of such ramps only.

3.	A 4-inch (102 mm) inspection space above patio and garage slabs and entry areas.

4.	If the patio has been soil treated for termites, the finish elevation may match the building interior finish floor elevations on masonry construction only.

5.	Masonry veneers.

CHAPTER 8

CHIMNEYS AND VENTS

Add an exception to R801.1 as shown:

R801.1 Application. The provisions of this chapter shall control the design and construction of the roof-ceiling system for all buildings (see Section R301.2.1.1).

Exception: Buildings and structures located within the High-Velocity Hurricane Zone shall comply with the provisions of Chapter 44.

Add general requirements to R802.1 and renumber rest as follows:

R802.1 General Requirements. Roof and ceiling framing of wood construction shall be designed and constructed in accordance with the provisions of this Section.

R802.1.1 [IRC R802.1]  Identification. [No change to text]

R802.1.2 [IRC R802.1.1] Blocking. [No change to text]

R802.1.3 [IRC R802.1.2] End-jointed lumber. Approved end-jointed lumber identified by a grade mark conforming to Section R802.1.1 may be used interchangeably with solid-sawn members of the same species and grade.

R802.1.4  [IRC R802.1.3] Fire-retardant-treated wood. [No change to text]

R802.1.4.1 [IRC R802.1.3.1] Pressure process. For wood products impregnated with chemicals by a pressure process, the process shall be performed in closed vessels under pressures not less than 50 pounds per square inch gauge (psig) (344.7 kPa).

R802.1.4.2 [IRC R802.1.3.2] Other means during manufacture. For wood products produced by other means during manufacture the treatment shall be an integral part of the manufacturing process of the wood product. The treatment shall provide permanent protection to all surfaces of the wood product.

R802.1.4.3 [IRC R802.1.3.3]Testing. For wood products produced by other means during manufacture, other than a pressure process, all sides of the wood product shall be tested in accordance with and produce the results required in Section R802.1.43. Testing of only the front and back faces of wood structural panels shall be permitted.

R802.1.4.4 [IRC R802.1.3.4] Labeling. Fire-retardant-treated lumber and wood structural panels shall be labeled. The label shall contain:

1 – 6 [No change from IRC].

7. Conformance with appropriate standards in accordance with Sections R802.1.4.5 through R802.1.4.8.

8. [No change from IRC.]

R802.1.4.5 [IRC R802.1.3.5] Strength adjustments. [No other change to IRCtext]

R802.1.4.5.1 [ IRC R802.1.3.5.1] Wood structural panels. [No other change to IRCtext]

R802.1.4.5.2 [IRC R802.1.3.5.2] Lumber. [No other change to IRCtext]

R802.1.4.6 [IRC R802.1.3.6] Exposure to weather. [No other change to IRCtext]

R802.1.4.7 [IRC R802.1.3.7] Interior applications. Interior fire retardant- treated wood … in accordance with Section R802.1.4.5.1 or R802.1.4.5.2...of this section.

R802.1.4.8 [IRC R802.1.3.8] Moisture content. Fire-retardant-treated wood shall be dried … in Section R802.1.4.5.1 for plywood and R802.1.4.5.2 for lumber.

802.1.5  [IRC R802.1.4] Structural glued laminated timbers. [No other change from IRC.]

R802.1.6  [IRC R802.10] Wood trusses.

R802.1.6.1 Truss design drawings. Truss design drawings, prepared in conformance with Section R802.1.6.1, shall be provided to the building official and approved prior to installation. Truss design drawings shall include, at a minimum, the information specified below. Truss design drawing shall be provided with the shipment of trusses delivered to the jobsite.

1. Design wind speed and exposure category.

2. Slope or depth, span and spacing.

3. Location of all joints.

4. Required bearing widths.

5. Design loads as applicable.

5.1 Top chord live load (as determined from Section R301.6).

5.2 Top chord dead load.

5.3 Bottom chord live load.

5.4 Bottom chord dead load.

5.5 Concentrated loads and their points of application.

5.6 Controlling wind and earthquake loads.

6. Adjustments to lumber and joint connector design values for conditions of use.

7. Each reaction force and direction.

8. Joint connector type and description (e.g., size, thickness or gauge) and the dimensioned location of each joint connector except where symmetrically located relative to the joint interface.

9. Lumber size, species and grade for each member.

10. Connection requirements for:

10.1 Truss to truss girder.

10.2 Truss ply to ply.

10.3 Field splices.

11. Calculated deflection ratio and/or maximum description for live and total load.

12. Maximum axial compression forces in the truss members to enable the building designer to design the size, connections and anchorage of the permanent continuous lateral bracing. Forces shall be shown on the truss design drawing or on supplemental documents.

13. Required permanent truss member bracing location.

R802.1.6.2 [IRC R802.10.2] Design. Wood trusses shall be designed in accordance with accepted engineering practice. The design and manufacture of metal-plate-connected wood trusses shall comply with ANSI/TPI 1. The truss design drawings shall be prepared by a registered professional where required by Florida Statutes.

R802.1.6.2.1 [IRC R802.10.2.1] Applicability limits. The provisions of this section shall control the design of truss roof framing when snow controls for buildings not greater than 60 feet (18 288 mm) in length perpendicular to the joist, rafter or truss span, not greater than 36 feet (10 973 mm) in width parallel to the joist, rafter or truss span, not greater than two stories in height with each story not greater than 10 feet (3048 mm) high, and roof slopes not smaller than 3:12 (25-percent slope) or greater than 12:12 (100-percent slope). Truss roof framing constructed in accordance with the provisions of this section shall be limited to sites subjected to a maximum design wind speed of

110 miles per hour (49 m/s), Exposure A, B or C, and a maximum ground snow load of 70 psf (3352 Pa). For consistent loading of all truss types, roof snow load is to be computed as: 0.7 pg.

Section R802.6.3 Bracing.  Change to read as shown.

R802.1.6.3 [IRC R802.10.3] Bracing. Trusses shall be braced to prevent rotation and provide lateral stability in accordance with the requirements specified in the construction documents for the building and on the individual truss design drawings. In the absence of specific bracing requirements, trusses shall be braced in accordance with TPI/WTCA BCSI.

R802.1.6.4 [IRC R802.10.4] Alterations to trusses. [No other change to IRC text]

R802.1.6.5 [IRC R802.10.5]  Truss to wall connection. Trusses shall be connected to wall plates by the use of approved connectors having a resistance to design uplift, lateral and shear forces. Trusses shall be installed in accordance with the manufacturer’s design and specifications. For roof assemblies subject to wind uplift pressures of 20 pounds per square foot (0.958 kN/m2) or greater, as established in Table R301.2(2), adjusted for height and exposure per Table R301.2(3), see Section R802.2.9.

Change R802.2 as shown:

R802.2 Design and construction where wind speed is less than 100 mph. The framing details required in Section R802 apply to roofs having a minimum slope of three units vertical in 12 units horizontal (25-percent slope) or greater. Roof-ceilings of conventional light-frame wood construction shall be designed and constructed in accordance with the provisions of this Section. Alternately, roof-ceilings may be designed and constructed in accordance with AF&PA”s NDS or AF&PA’s WFCM. Components of roof-ceilings shall be fastened in accordance with Table R602.2(1).

R802.2.1 [IRC R802.3] Framing details. [No other change to IRC text, R802.3]

R802.2.1.1  [ IRC R802.3.1] Ceiling joist and rafter connections. Ceiling joists and rafters shall be nailed to each other in accordance with Tables R602.2(1) and R802.2.3(9) and the assembly shall be nailed to the top wall plate in accordance with Table R602.2(1). Ceiling joists shall be continuous or securely joined where they meet over interior partitions and nailed to adjacent rafters to provide a continuous tie across the building when such joists are parallel to the rafters.

Where ceiling joists are not connected to the rafters at the top wall plate, joists connected higher in the attic shall be installed as rafter ties, or rafter ties shall be installed to provide a continuous tie. Where ceiling joists are not parallel to rafters, rafter ties shall be installed. Rafter ties shall be a minimum of 2-inch by 4-inch (51 mm by 102 mm) (nominal), installed in accordance with the connection requirements in Table R802.5.1(9), or connections of equivalent capacities shall be provided. Where ceiling joists or rafter ties are not provided, the ridge formed by these rafters shall be supported by a wall or girder designed in accordance with accepted engineering practice.

Collar ties or ridge straps to resist wind uplift shall be connected in the upper third of the attic space in accordance with Table R602.2(1).

Collar ties shall be a minimum of 1-inch by 4-inch (25 mm by 102 mm) (nominal), spaced not more than 4 feet (1219 mm) on center.

R802.2.1.2  [IRC R802.3.2] Ceiling joists lapped. Ends of ceiling joists shall be lapped a minimum of 3 inches (76 mm) or butted over bearing partitions or beams and toe nailed to the bearing member. When ceiling joists are used to provide resistance to rafter thrust, lapped joists shall be nailed together in accordance with Table R602.2(1) and butted joists shall be tied together in a manner to resist such thrust.

R802.2.2  [IRC R802.5] Allowable ceiling joist spans. Spans for ceiling joists shall be in accordance with Tables R802.2(1) and R802.2(2). For other grades and species and for other loading conditions, refer to the AF&PA Span Tables for Joists and Rafters.

Table R802.2(1) [Use IRC’ Table R802.4(1); only change is number]

Table R802.2(2) [Use IRC’ Table R802.4(2); only change is number]

R802.2.3  Allowable rafter spans. [IRC 802.5] Spans for rafters shall be in accordance with Tables R802.2.3(1) through R802.2.3(8). For other grades and species and for other loading conditions, refer to the AF&PA Span Tables for Joists and Rafters. The span of each rafter shall be measured along the horizontal projection of the rafter.

R802.2.3.1  [IRC R802.5.1] Purlins. Purlins are permitted to be installed to reduce the span of rafters as shown in Figure R802.2.3.1. Purlins shall be sized … braces shall not exceed 8 feet (2438 mm).

Table R802.2.3(1) [Use IRC’ Table R802.5.1(1); only change is number]

Table R802.2.3(2) [Use IRC’ Table R802.5.1(2); only change is number]

Table R802.5.1(3) Rafter Spans for Common Lumber Species (Ground snow load = 30 psf, ceiling not attached to rafters, L/ = 180)  Reserved.

Table R802.5.1(4) Rafter Spans for Common Lumber Species (Ground snow load = 50 psf, ceiling not attached to rafters, L/ = 180) Reserved.

Table R802.5.1(5) Rafter Spans for Common Lumber Species (Ground snow load = 30 psf, ceiling not attached to rafters, L/ = 240) Reserved.

Table R802.5.1(6) Rafter Spans for Common Lumber Species (Ground snow load = 50 psf, ceiling not attached to rafters, L/ = 240) Reserved.

Table R802.5.1(7) Rafter Spans for 70 PSF Ground Snow Load (Ceiling not attached to rafters, L/ = 180) Reserved.

Table R802.5.1(8) Rafter Spans for 70 PSF Ground Snow Load (Ceiling not attached to rafters, L/ = 180) Reserved.

Table R802.2.3(9) [Use IRC’ Table R802.5.1(9);with snow load removed]]

R802.2.4  Bearing. [Use IRC’ R802.6; only change is number]

R802.2.5  Finished ceiling material. [Use IRC R802.6.1’; only change is number]

R802.2.6  Cutting and notching. [Use IRC’, R802.7; only change is number]

R802.2.6.1  Sawn lumber. [Use IRC R802.7.1’; only change is number]

802.2.6.2  [IRC R802.7.2]Engineered wood products. Cuts, notches and holes bored in trusses, structural composite lumber, structural glue-laminated members or I-joists are prohibited except where permitted by the manufacturer’s recommendations or where the effects of such alterations are specifically considered in the design of the member by a registered design professional.

R802.2.7  Lateral support. [Use IRC’ R802.8; only change is number]

R802.2.7.1  Bridging.  [Use IRC R802.8.1 only change is number]

R802.2.8  Framing of openings. [Use IRC’ R802.9; only change is number]

R802.2.9  Roof tie-down. [Use IRC’ R802.11]

R802.2.9.1  [IRC R802.11.1] Uplift resistance. Roof assemblies which are subject to wind uplift pressures of 20 pounds per square foot (0.958 kN/m2) or greater shall have roof rafters or trusses attached to their supporting wall assemblies by connections capable of providing the resistance required in Table R802.2.9.1. Wind uplift pressures shall be determined using an effective wind area of 100 square feet (9.3m2) and Zone 1 in Table R301.2(2), as adjusted for height and exposure per Table R301.2(3).

A continuous load path shall be provided to transmit the uplift forces from the rafter or truss ties to the foundation. For rafter construction, straps and/or clips shall extend such that the top nail is within 1 inch of the top of the rafter, or shall be wrapped around the top of the rafter with one or more nails installed on the opposite side of the rafter.

Table R802.2.9.1 Roof Bearing Uplift at Top of Wall in Exposure B PLF, revise text to read as follows:

|  | TABLE R802.2.9.1 |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | ROOF BEARING UPLIFT AT TOP OF WALL IN EXPOSURE B, PLF1,2,4 |  |  |  |  |  |  |  |  |
| Roof Angle | Wind Speed, mph | Roof Span (feet) |  |  |  |  |  |  | Over-hangs3 |
|  |  | 12 | 20 | 24 | 28 | 32 | 36 | 40 |  |
| End zone load for all roof angles | 85 | -39.50 | -65.83 | -79.00 | -92.16 | -105.33 | -118.49 | -131.66 | -19.3 |
|  | 90 | -48.64 | -81.07 | -97.28 | -113.50 | -129.71 | -145.92 | -162.14 | -21.6 |
|  | 100 | -68.50 | -114.16 | -136.99 | -159.82 | -182.66 | -205.49 | -228.32 | -26.7 |
|  | 110 | -90.44 | -150.73 | -180.88 | -211.03 | -241.17 | -271.32 | -301.47 | -32.3 |
|  | 120 | -114.47 | -190.79 | -228.95 | -267.11 | -305.26 | -343.42 | -381.58 | -38.4 |
|  | 130 | -140.60 | -234.33 | -281.20 | -328.06 | -374.93 | -421.79 | -468.66 | -45.1 |
|  | 140 | -168.81 | -281.35 | -337.62 | -393.89 | -450.16 | -506.44 | -562.71 | -52.3 |
|  | 150 | -199.12 | -331.86 | -398.23 | -464.60 | -530.97 | -597.35 | -663.72 | -60.0 |
| Interior zone load for all roof angles | 85 | -17.57 | -29.28 | -35.13 | -40.99 | -46.84 | -52.70 | -58.55 | -15.1 |
|  | 90 | -24.05 | -40.09 | -48.11 | -56.12 | -64.14 | -72.16 | -80.18 | -16.9 |
|  | 100 | -38.14 | -63.57 | -76.28 | -88.99 | -101.71 | -114.42 | -127.13 | -20.9 |
|  | 110 | -53.71 | -89.52 | -107.42 | -125.32 | -143.22 | -161.13 | -179.03 | -25.3 |
|  | 120 | -70.76 | -117.94 | -141.52 | -165.11 | -188.70 | -212.28 | -235.87 | -30.1 |
|  | 130 | -89.30 | -148.83 | -178.59 | -208.36 | -238.12 | -267.89 | -297.65 | -35.3 |
|  | 140 | -109.31 | -182.19 | -218.63 | -255.07 | -291.50 | -327.94 | -364.38 | -40.9 |
|  | 150 | -130.81 | -218.02 | -261.63 | -305.23 | -348.84 | -392.44 | -436.05 | -47.0 |
| Interior zone uplift for 300 roof angle |  |  |  |  |  |  |  |  |  |
|  |  |  | All values deleted |  |  |  |  |  |  |

|  | TABLE R802.2.9.1 (cont.) |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | ROOF BEARING UPLIFT AT TOP OF WALL IN EXPOSURE C, PLF1,2,4 |  |  |  |  |  |  |  |  |
| Roof Angle | Wind Speed, mph | Roof Span (feet) |  |  |  |  |  |  | Over-hangs3 |
|  |  | 12 | 20 | 24 | 28 | 32 | 36 | 40 |  |
| End zone load for all roof angles | 85 | -69.85 | -116.42 | -139.70 | -162.99 | -186.27 | -209.55 | -232.84 | -27.0 |
|  | 90 | -82.67 | -137.78 | -165.34 | -192.90 | -220.45 | -248.01 | -275.57 | -30.3 |
|  | 100 | -110.51 | -184.18 | -221.01 | -257.85 | -294.68 | -331.52 | -368.36 | -37.4 |
|  | 110 | -141.27 | -235.45 | -282.55 | -329.64 | -376.73 | -423.82 | -470.91 | -45.3 |
|  | 120 | -174.97 | -291.62 | -349.94 | -408.26 | -466.59 | -524.91 | -583.23 | -53.9 |
|  | 130 | -211.60 | -352.66 | -423.19 | -493.72 | -564.26 | -634.79 | -705.32 | -63.2 |
|  | 140 | -251.15 | -418.59 | -502.31 | -586.02 | -669.74 | -753.46 | -837.18 | -73.3 |
|  | 150 | -293.64 | -489.40 | -587.28 | -685.16 | -783.04 | -880.92 | -978.80 | -84.2 |
| Interior zone load for all roof angles | 85 | -39.10 | -65.17 | -78.20 | -91.24 | -104.27 | -117.30 | -130.34 | -21.2 |
|  | 90 | -48.20 | -80.33 | -96.39 | -112.46 | -128.52 | -144.59 | -160.66 | -23.7 |
|  | 100 | -67.95 | -113.24 | -135.89 | -158.54 | -181.19 | -203.84 | -226.49 | -29.3 |
|  | 110 | -89.78 | -149.63 | -179.55 | -209.48 | -239.40 | -269.33 | -299.25 | -35.4 |
|  | 120 | -113.68 | -189.47 | -227.37 | -265.26 | -303.16 | -341.05 | -378.94 | -42.2 |
|  | 130 | -139.67 | -232.78 | -279.34 | -325.90 | -372.45 | -419.01 | -465.57 | -49.5 |
|  | 140 | -167.74 | -279.56 | -335.47 | -391.38 | -447.29 | -503.21 | -559.12 | -57.4 |
|  | 150 | -197.88 | -329.80 | -395.76 | -461.72 | -527.68 | -593.64 | -659.60 | -65.9 |
| Interior zone uplift for 300 roof angle |  |  |  |  |  |  |  |  |  |
|  |  |  | All values deleted. |  |  |  |  |  |  |

Notes:

a. The uplift loads are pounds per lineal foot of building length. For roof uplift connections use the tables for 20 degrees and multiply by 1.33 for framing spaced 16 inches on center and multiply by 2 for framing spaced 24 inches on center.

b. The uplift loads include an allowance for 10 pounds of dead load.

c. The uplift loads do not account for the effects of overhangs. The magnitude of the above loads shall be increased by adding the overhang loads found in the table. The overhang loads are also based on framing spaced 12 inches on center. The overhang loads given shall be multiplied by the overhang projection and added to the roof uplift value in the table.

d. End zones extend 8 feet from building corners.

e. For buildings with a roof slope of 5:12 or greater, tabulated uplift loads shall be permitted to be multiplied by 0.87.

f. Negative values indicate uplift.

g. Reserved.

## Table R802.2.9.1 WIND UPLIFE FORCES EXPOSURE B, EXPOSURE C [Replace Table R802.11; Use FL specific tables in their entirety]

R802.3 Design and construction where wind speed is 100 mph or greater. Roof-ceilings of light-frame wood construction shall be designed and constructed in accordance with the provisions of Section R301.2.1.1 and Section R802.1.

R803.1Lumber sheathing. Allowable spans for lumber used as roof sheathing shall conform to Table R803.1. Spaced lumber sheathing for wood shingle and shake roofing shall conform to the requirements of Sections R905.7 and R905.8. Spaced lumber sheathing is not allowed in Seismic Design Category D2.

Change R803.2.3 as shown:

R803.2.3 Installation. Wood structural panels used as roof sheathing shall be installed with joints staggered in accordance with Section R803.2.3.1 for wood roof framing or with Table R804.3 for steel roof framing in accordance with the applicability limits established in Section R804.1.1.

R803.2.3.1 Sheathing fastenings.  Wood structural panel sheathing shall be fastened to roof framing with 8d ring-shank nails at 6 inches on center at edges and 6 inches on center at intermediate framing.  Ring-shank nails shall have the following minimum dimensions:

- 0.113 inch nominal shank diameter

- Ring diameter of 0.012 over shank diameter

- 16 to 20 rings per inch

- 0.280 inch full round head diameter

- 2 inch nail length

Where roof framing with a specific gravity, 0.42 ≤ G < 0.49 is used, spacing of ring-shank fasteners shall be 4 inches on center in nailing zone 3 for 130 mph or greater design wind speeds in accordance with Figure R803.2.3.1.

Exceptions:

## 1. Where roof framing with a specific gravity, 0.42 ≤ G < 0.49 is used, spacing of ring-shank fasteners shall be permitted at 12 inches on center at intermediate framing in nailing zone 1 for any design wind speed and in nailing zone 2 for 110 mph or lower design wind speeds in accordance with Figure R803.2.3.1.

2. Where roof framing with a specific gravity, G ≥ 0.49 is used, spacing of ring-shank fasteners shall be permitted at 12 inches on center at intermediate framing in nailing zone 1 for any design wind speed and in nailing zone 2 for 120 mph or lower design wind speeds in accordance with Figure R803.2.3.1.

3.  Where roof framing with a specific gravity, G ≥ 0.49 is used, 8d common or 8d hot dipped galvanized box nails at 6 inches on center at edges and 6 inches on center at intermediate framing shall be permitted for 100 mph or lower design wind speeds in accordance with Figure R803.2.3.1.

4.  Where roof diaphragm requirements necessitate a closer fastener spacing.

FIGURE R803.2.3.1  ROOF SHEATHING NAILING ZONES

[Use FL specific figure]

Change R804 as shown:

R804.1.1 Applicability limits. The provisions of this section shall control the construction of cold-formed steel roof framing for buildings not greater than 60 feet (18 288 mm) in length perpendicular to the joist, rafter or truss span, not greater than 3640 feet (12 192 mm) in width parallel to the joist span or truss, less than or equal to three stories above grade plane with each story not greater than 10 feet (3048 mm) high and with roof slopes not less than 3:12 (25-percent slope) or greater than 12:12 (100 percent slope). Cold-formed steel roof framing constructed in accordance with the provisions of this section shall be limited to sites subjected to a maximum design wind speed of 110 miles per hour (49 m/s), Exposure  B or C.

R804.2.5 Web holes….

R804.3.2.1 Minimum roof rafter sizes. Roof rafter size and thickness shall be determined in accordance with the limits set forth in Tables R804.3.2.1(1) and R804.3.2.1(2) based on the horizontal projection of the roof rafter span. For determination of roof rafter sizes, reduction of roof spans shall be permitted when a roof rafter support brace is installed in accordance with Section R804.3.2.2. The reduced roof rafter span shall be taken as the larger of the distance from the roof rafter support brace to the ridge or to the heel measured horizontally. For the purpose of determining roof rafter sizes in Tables R804.3.2.1(1) and R804.3.2.1(2), wind speeds shall be converted to equivalent ground snow loads in accordance with Table R804.3.2.1(3). Roof rafter sizes shall be based on the higher of the ground snow load or the equivalent snow load converted from the wind speed.

R804.3.3 Hip framing. Hip framing shall consist of jack-rafters, hip members, hip support columns and connections in accordance with this section, or shall be in accordance with an approved design. The provisions of this section for hip members and hip support columns shall apply only where the jack rafter slope is greater than or equal to the roof slope. For the purposes of determining member sizes in this section, wind speeds shall be converted to equivalent ground snow load in accordance with Table R804.3.2.1(3).

TABLE R804.3.1.1(9)

NUMBER OF SCREWS REQUIRED FOR CEILING JOIST TO ROOF RAFTER CONNECTIONa  (Remove snow load)

TABLE R804.3.2.1(1)

ROOF RAFTER SPANSa, b, c

33 ksi STEEL  (Reserved)

TABLE R804.3.2.1(2)

ROOF RAFTER SPANSa, b, c

50 ksi STEEL   (Reserved)

TABLE R804.3.2.1(3)

BASIC WIND SPEED TO EQUIVALENT SNOW LOAD CONVERSION   (Reserved)

TABLE R804.3.2.4

SCREWS REQUIRED AT EACH LEG OF CLIP ANGLE FOR HIP RAFTER

TO HIP MEMBER OR ROOF RAFTER TO RIDGE MEMBER CONNECTIONa  (Remove snow load)

TABLE R804.3.3.2

HIP MEMBER SIZES, 33 ksi STEEL  (Remove snow load)

TABLE R804.3.3.3

HIP SUPPORT COLUMN SIZES   (Remove snow load)

TABLE R804.3.3.4(2)

CONNECTION REQUIREMENTS

HIP MEMBER TO HIP SUPPORT COLUMN   (Remove snow load)

Section R806.1 Ventilation required. Change to read as shown.

R806.1 Ventilation required. Enclosed attics and enclosed rafter spaces formed where ceilings are applied directly to the underside of roof rafters shall have cross ventilation for each separate space by ventilating openings protected against the entrance of rain or snow. Ventilation openings shall have a least dimension of 1/16 inch (1.6 mm) minimum and 1/4 inch (6.4 mm) maximum. Ventilation openings having a least dimension larger than 1/4 inch (6.4 mm) shall be provided with corrosion-resistant wire cloth screening, hardware cloth, or similar material with openings having a least dimension of 1/16 inch (1.6 mm) minimum and 1/4 inch (6.4 mm) maximum. Openings in roof framing members shall conform to the requirements of SectionR802.7.

Exception: Attic spaces, designed by a professional engineer or architect licensed to practice in the state, designed to eliminate the attic venting.

Overlap with Florida Specific – Structural TAC/Mechanical TAC

FBC

Section R806.4 Conditioned attic assemblies.  Change to read as shown. Need to be resolved.

R806.4 Unvented attic assemblies. Unvented attic assemblies shall be permitted if all the following conditions are met:

1. The unvented attic space is completely contained within the building thermal envelope.

2. No interior vapor retarder is installed on the ceiling side (attic floor) of the unvented attic assembly.

3.Where  wood shingles or shakes are used, a minimum continuous ¼ inch (6 mm) vented air space separates the shingles or shakes from the roofing underlayment.

4. One of the following: shall be met, depending on the air permeability of the insulation under the structural roof sheathing.

a. Air-impermeable insulation only. Insulation shall be applied in direct contact to the underside of the structural roof sheathing.

b. Air-permeable insulation only. In addition to air-permeable insulation installed directly below the structural sheathing, at least R-5 rigid board or sheet insulation shall be installed directly above the structural roof sheathing for condensation control.

c. Air-impermeable and air-permeable insulation. At least R-5 air-impermeable insulation shall be applied in direct contact to the underside of the structural roof sheathing for condensation control. The air-permeable insulation shall be installed directly under the air-impermeable insulation.

R806.4 Unvented attic assemblies. Unvented attic assemblies (spaces between the ceiling joists of the top story and the roof rafters) shall be permitted if all the following conditions are met:

1. The unvented attic space is completely contained within the building thermal envelope.

2. No interior vapor retarders are installed on the ceiling side (attic floor) of the unvented attic assembly.

3. Where wood shingles or shakes are used, a minimum1/4 inch (6 mm) vented air space separates the shingles or shakes and the roofing underlayment above the structural sheathing.

4. In climate zones 5, 6, 7 and 8, any air-impermeable insulation shall be a vapor retarder, or shall have a vapor retarder coating or covering in direct contact with the underside of the insulation.

5. Either Items 5.1, 5.2 or 5.3 shall be met, depending on the air permeability of the insulation directly under the structural roof sheathing.

5.1. Air-impermeable insulation only. Insulation shall be applied in direct contact with the underside of the structural roof sheathing.

5.2. Air-permeable insulation only. In addition to the air-permeable installed directly below the structural sheathing, rigid board or sheet insulation shall be installed directly above the structural

roof sheathing as specified in Table R806.4 for condensation control.

5.3. Air-impermeable and air-permeable insulation. The air-impermeable insulation shall be applied in direct contact with the underside of the structural roof sheathing as specified in Table R806.4 for condensation control. The air-permeable insulation shall be installed directly under the air-impermeable insulation.

Staff  recommendation: The IRC09 does not cover Florida specific provisions. Recommend retaining Florida specific provisions as stated above.

CHAPTER 9

ROOF ASSEMBLIES

Add exception to R901.1 as shown:

R901.1 Scope.  The provisions of this chapter shall govern the design, materials, construction and quality of roof assemblies.

Exception: Buildings and structures located within the High-Velocity Hurricane Zone shall comply with the provisions of Chapter 44.

Overlap with Florida Specific - Roofing TAC

Add exception to R902.1 as shown: Need to be resolved.

FBC

R902.1 Roofing covering materials. Roofs shall be covered with materials as set forth in Sections R904 and R905.  Class A, B or C roofing shall be installed in areas designated by law as requiring their use or when the edge of the roof is less than 3 feet (914 mm) from a property line. Classes A, B and C roofing required to be listed by this section shall be tested in accordance with UL 790 or ASTM E 108.

Exception:  Brick, masonry, slate, clay or concrete roof tile; ferrous and copper shingles and shakes; and exposed concrete roof deck are considered to meet Class A roof covering provisions without testing.  Metal sheets and shingles are considered to meet Class B roof covering provisions without testing.

2009 IRC

Exceptions:

1. Class A roof assemblies include those with coverings of brick, masonry and exposed concrete roof deck.

2. Class A roof assemblies also include ferrous or copper shingles or sheets, metal sheets and shingles, clay or concrete roof tile, or slate installed on noncombustible decks.

Staff  recommendation: The IRC09 does not cover Florida specific provisions. Recommend retaining Florida specific provisions as stated above.

Section R903.2.1 Locations.  Change to read as shown:

R903.2.1 Locations. Flashings shall be installed at wall and roof intersections, wherever there is a change in roof slope or direction and around roof openings. Where flashing is of metal, the metal shall be corrosion resistant with a thickness of not less than provided in Table R903.2.1.

Exception: Flashing is not required at hip and ridge junctions.

TABLE R903.2.1 METAL FLASHING MATERIAL

| MATERIAL | GAGE MINIMUM THICKNESS (INCHES) | GAGE | WEIGHT (lbs per sq ft) |
| --- | --- | --- | --- |
| Copper | 0.024 |  | 1 (16 oz) |
| Aluminum | 0.024 |  | 28 |
| Stainless Steel |  | 28 |  |
| Galvanized Steel |  | 26 (zinc |  |
|  | 0.0179 | coated G90) | 26 (zinc coated G90) |
| Aluminum Zinc |  | 26 (AZ50 |  |
| Coated Steel | 0.0179 | Alum Zinc) | 26 (AZ50 Alum Zinc) |
| Zinc Alloy | 0.027 |  |  |
| Lead |  |  | 2.5 (40 oz) |
| Painted Terne |  |  | 1.25 (20 oz) |

R903.2.2 Crickets and saddles.  A cricket or saddle shall be installed on the ridge side of any chimney greater than 30 inches (762 mm) wide. Cricket or saddle coverings shall be sheet metal or of the same material as the roof covering.

R903.2.3 Membrane flashings. All membrane flashing shall be installed according to the roof assembly manufacturer’s published literature.

Section R903.3 Coping.  Change to read as shown.

R903.3 Coping.  Parapet walls shall be properly coped with noncombustible, weatherproof materials of a width no less than the cross section of the parapet wall. Metal coping shall comply with ANSI/SPRI/ ES-1 or RAS 111.

R903.4.1 When other means of drainage of overflow water is not provided, overflow scuppers shall be placed in walls or parapets not less than 2 inches (51 mm) nor more than 4 inches (102 mm) above the finished roof covering and shall be located as close as practical to required vertical leaders or downspouts or wall and parapet scuppers. An overflow scupper shall be sized in accordance with the Florida Building Code, Plumbing.

Section R903.5 Hail exposure.  Change to read as shown.

R903.5  Hail exposure.  Reserved.

Section R903.5.1 One and two family dwellings, and private garages.  Add to read as shown.

R903.5.1  One and two family dwellings, and private garages. When gutters and leaders are placed on the outside of buildings, the gutters and leaders shall be constructed of metal or approved plastic for outdoor exposure with lapped, soldered or caulked joints and shall be securely fastened to the building with a corrosion resistant fastening device of similar or compatible material to the gutters and downspouts.

Change R904 as shown:

R904.4.  Fasteners.

R904.4.1. Nails. Nails shall be corrosion resistant nails conforming to ASTM F 1667.  The corrosion resistance shall meet ASTM A 641, Class I or an equal corrosion resistance by coating, electro galvanization, mechanical galvanization, hot dipped galvanization, stainless steel, nonferrous metal and alloys or other suitable corrosion-resistant material.

Section R904.4.2 Screws.  Add to read as shown.

R904.4.2. Screws. Wood screws shall conform to ANSI/ASME B 18.6.1.  Screws shall be corrosion resistant.  by coating, galvanization, stainless steel, nonferrous metal or other suitable corrosion resistant material.  The corrosion resistance shall be demonstrated through one of the following methods:

1.  Corrosion resistance equivalent to ASTM A 641, Class 1; or,

2.  Corrosion resistance in accordance with TAS 114, Appendix E; or,

3.  Corrosion resistant coating exhibiting not more than 5% red rust after 1000 hours exposure in accordance with ASTM B 117.

Section R904.4.3 Clips.  Add to read as shown.

R904.4.3 Clips.  Clips shall be corrosion resistant clips.  The corrosion resistance shall meet  0.90 oz per sq ft (0.458 kg/m2) measured according  ASTM A 90/A 90M, TAS 114 Appendix E  or an equal corrosion resistance coating, electro galvanization, mechanical galvanization, hot dipped galvanization, stainless steel, nonferrous metals and alloys or other suitable corrosion resistant material.  Stainless steel clips shall conform to ASTM A167, Type 304.

R904.5 Product identification.  Roof covering materials shall be delivered in packages bearing the manufacturer’s identifying marks and approved testing agency labels when required. Bulk shipments of materials shall be accompanied by the same information issued in the form of a certificate or on a bill of lading by the manufacturer.

Change R905.2.2 as shown:

R905.2.2 Slope. Asphalt shingles shall only be used on roof slopes of two units vertical in 12 units horizontal (2:12) or greater. For roof slopes from two units vertical in 12 units horizontal (2:12) up to four units vertical in 12 units horizontal (4:12), two layers of underlayment complying with ASTM D226, Type I or Type II, ASTM D 4869, Type I or Type II or ASTM D6757 is required in accordance with Section R905.2.7.

R905.2.3 Underlayment. Unless otherwise noted, required underlayment shall conform with ASTM D 226 Type I or Type II, ASTM D 4869, Type I or Type II, or ASTM D6757.

Self-adhering polymer modified bitumen sheet shall comply with ASTM D 1970.

Overlap with Florida Specific – Roofing TAC

Section R905.2.4.1 Wind resistance of asphalt shingles revise text to read as follows: Need to be resolved.

FBC

R905.2.4.1 Wind resistance of asphalt shingles.  Asphalt shingles shall be installed in accordance with Section R905.2.6. and R905.2.6.1.

2009 IRC

R905.2.4 Asphalt shingles. Asphalt shingles shall comply with ASTM D 225 or D 3462.

R905.2.4.1Wind resistance of asphalt shingles. Asphalt shingles shall be tested in accordance with ASTM D 7158. Asphalt shingles shall meet the classification requirements of Table R905.2.4.1(1) for the appropriate maximum basic wind speed. Asphalt shingle packaging shall bear a label to indicate compliance with ASTM D 7158 and the required

classification in Table R905.2.4.1(1).

Exception: Asphalt shingles not included in the scope of ASTM D 7158 shall be tested and labeled to indicate compliance with ASTM D 3161 and the required classification in Table R905.2.4.1(2).

Staff  recommendation: The IRC09 does not cover Florida specific provisions. Recommend retaining Florida specific provisions as stated above.

R905.2.5  Fasteners. Fasteners for asphalt shingles shall be galvanized steel, stainless steel, aluminum or copper roofing nails, minimum 12 gage [0.105 inch (2.67 mm)] shank with a minimum 3/8-inch (9.5 mm) diameter head, ASTM F 1667, of a length to penetrate through the roofing materials and a minimum of ¾ inch (19.1 mm) into the roof sheathing. Where the roof sheathing is less than ¾ inch (19.1 mm) thick, the fasteners shall penetrate through the sheathing. Fasteners shall comply with ASTM F 1667.

Exception:  If the architectural appearance is to be preserved from below, an alternate method of attachment complying with the wind load requirements of Chapter 16 of the Florida Building Code, Building may be proposed unless otherwise addressed in Chapter 9.  The alternative attachment shall be prepared, signed and sealed by a Florida-registered architect or a Florida-registered engineer, which architect or engineer shall be proficient in structural design.

R905.2.5.1 The nail component of plastic cap nails shall meet ASTM A 641, Class I or an equal corrosion resistance by coating, electro galvanization, mechanical galvanization, hot dipped galvanization, stainless steel, nonferrous metal and alloys or other suitable corrosion-resistant material.

R905.2.6 Attachment. Asphalt shingles shall have the minimum number of fasteners required by the manufacturer, but not less than four fasteners per strip shingle or two fasteners per individual shingle. Where the roof slope, exceeds 21 units vertical in 12 units horizontal (21:12, 175 percent slope), shingles shall be installed as required by the manufacturer.

R905.2.6.1 Wind Resistance of Asphalt Shingles. Asphalt Shingles shall be classified in accordance with ASTM D3161, TAS 107 or ASTM D7158 to resist the basic wind speed per Figure R301.2 (4). Shingles classified as ASTM D 3161 Class D or classified as ASTM D 7158   Class G are acceptable for use in the 100-mph wind zone. Shingles classified as ASTM D3161 Class F, TAS107 or ASTM D 7158 Class H are acceptable for use in all wind zones.  Asphalt shingle wrappers shall indicate compliance with one of the required classifications as shown in Table R905.2.6.1.

Table R905.2.6.1

Wind Resistance of Asphalt Shingles

| Maximum Basic Wind Speed MPH (per Figure R301.2 (4) | Classification |
| --- | --- |
| 100 | ASTM D3161Class D or ASTM D 7158 Class G or TAS 107 |
| 110 | ASTM D3161Class F or ASTM D 7158 Class G or TAS 107 |
| 120 | ASTM D3161Class F or ASTM D 7158 Class G or TAS 107 |
| 130 | ASTM D3161Class F or ASTM D 7158 Class H or TAS 107 |
| 140 | ASTM D3161Class F or ASTM D 7158 Class H or TAS 107 |
| 150 | ASTM D3161Class F or ASTM D 7158 Class H or TAS 107 |

Table R905.2.4.1(1) & Table R905.2.4.1(2)

R905.2.7 Underlayment application. For roof slopes from two units vertical in 12 units horizontal (17-percent slope), up to four units vertical in 12 units horizontal (33-percent slope), two layers of underlayment complying with ASTM D226 Type I or Type II, ASTM D 4869 Type I or Type II, or ASTM D6757 shall be applied in the following manner:

- Apply a minimum 19-inch-wide (483 mm) strip of underlayment felt parallel with and starting at the eaves.

- Starting at the eave, apply 36-inch-wide (914 mm) sheets of underlayment overlapping successive sheets 19 inches (483 mm). Distortions in the underlayment shall not interfere with the ability of the shingles to seal.

- End laps shall be offset by 6 feet (1829 mm)

- Corrosion resistant fasteners are to be applied along the overlap at a maximum spacing of 36 inches (914 mm) on center.

For roof slopes of four units vertical in 12 units horizontal (33-percent slope) or greater, one layer of underlayment complying with ASTM D226 Type I or Type II, ASTM D 4869 Type I or Type II, or ASTM D6757 shall be applied in the following manner:

- Underlayment shall be applied shingle fashion, parallel to and starting from the eave and lapped 2 inches (51 mm).

- End laps shall be offset by 6 feet (1829 mm)

- Corrosion resistant fasteners are to be applied along the overlap at a maximum spacing of 36 inches (914 mm) on center.

R905.2.7.1 Ice protection. Reserved.

R905.2.7.2. Underlayment and high wind. Reserved.

R905.2.8.1 Base and counter flashing. Base and counter flashing shall be installed as follows:

1. In accordance with manufacturer’s installation instructions, or

2. A continuous metal minimum 4 inch by 4 inch “L” flashing shall be set in approved flashing cement and set flush to base of wall and over the underlayment. Both horizontal and vertical metal flanges shall be fastened 6 inches (152 mm) on center with approved fasteners. All laps shall be a minimum of 4 inches (102 mm) fully sealed in approved flashing cement. Flashing shall start at the lower portion of roof to ensure water-shedding capabilities of all metal laps. The entire edge of the horizontal flange shall be sealed covering all nail penetrations with approved flashing cement and membrane. Shingles shall overlap the horizontal flange and shall be set in approved flashing cement.

Base flashing shall be of either corrosion-resistant metal provided in Section R905.2.8.1 or mineral surface roll roofing weighing a minimum of 77 pounds per 100 square feet (3.76 kg/m2). Counter flashing shall be corrosion-resistant metal with a minimum thickness provided in Table R903.1.

Overlap with Florida Specific – Roofing TAC

Need to be resolved

FBC

R905.2.8.2 Valleys. Valley linings shall be installed in accordance with manufacturer’s installation instructions before applying shingles. Valley linings of the following types shall be permitted:

- For open valley lined with metal, the valley lining shall be at least 16 inches (406 mm) wide and of any of the corrosion-resistant metals in Table R903.1.

- For open valleys, valley lining of two plies of mineral surface roll roofing, complying with ASTM D 6380 Class M or ASTM D 3909, shall be permitted. The bottom layer shall be 18 inches (457 mm) and the top layer a minimum of 36 inches (914 mm) wide.

- For closed valleys, valley lining of one ply of smooth roll roofing complying with ASTM D 6380 Class S and at least 36 inches (914 mm) wide or valley lining as described in Items 1 or 2 above shall be permitted. Specialty underlayment complying with ASTM D 1970 may be used in lieu of the lining material.

2009 IRC

3. For closed valleys (valley covered with shingles), valley lining of one ply of smooth roll roofing complying with ASTM D 6380 Class S Type III, Class M Type II, or ASTM D 3909 and at least 36 inches wide (914 mm) or valley lining as described in Item 1 or 2 above shall be permitted. Self-adhering polymer modified bitumen Speciality underlayment complying with ASTM D 1970 shall may be permitted in lieu of the lining material.

Staff  recommendation: The IRC09 does not cover Florida specific provisions. Recommend retaining Florida specific provisions as stated above.

TABLE 905.2.8.2 VALLEY LINING MATERIALS

Reserved.

Overlap with Florida Specific – Roofing TAC

Section R905.2.8.3 Sidewall flashing.  Change to read as shown.  Need to be resolved.

FBC

R905.2.8.4 Sidewall flashing. Flashing against a vertical sidewall shall be by the step-flashing method or continuous “L” flashing method.

2009 IRC

R905.2.8.3 Sidewall flashing. Flashing against a vertical sidewall shall be by the step-flashing method. The flashing shall be a minimum of 4 inches (102 mm) high and 4 inches (102 mm) wide. At the end of the vertical sidewall the step flashing shall be turned out in a manner that directs water away from the wall and onto the roof and/or gutter.

Staff  recommendation: The IRC09 does not cover Florida specific provisions. Recommend retaining Florida specific provisions as stated above.

Section R905.2.8.4 Other flashing.  Change to read as shown.

R905.2.8.4 Other flashing. Reserved

R905.2.8.5  Drip edge.  Add to read as shown.

R905.2.8.5  Drip edge. Provide drip edge at eaves and gables of shingle roofs. Overlap to be a minimum of 3 inches (76 mm). Eave drip edges shall extend ½ inch (13 mm) below sheathing and extend back on the roof a minimum of 2 inches (51 mm).  Drip edge at eaves shall be permitted to be installed either over or under the underlayment.  If installed over the underlayment, there shall be a minimum 4 inch (51 mm) width of roof cement installed over the drip edge flange.  Drip edge shall be mechanically fastened a maximum of 12 inches (305 mm) on center.  Where the basic wind speed per Figure R301.2(4) is 110 mph (177 km/h) or greater or the mean roof height exceeds 33 feet (10 058 mm), drip edges shall be mechanically fastened a maximum of 4 inches (102 mm) on center.

Change R905.3 as shown:

R905.3  Clay and concrete tile.  The installation of clay and concrete shall be in accordance with recommendations of FRSA/TRI 07320 Manual.

R905.3.1 Deck requirements. Concrete and clay tile shall be installed only over solid sheathing, except where the roof covering is specifically designed and tested in accordance with Chapter 16, Florida Building Code, Building to be applied over structural spaced structural sheathing boards.

R905.3.2 Deck slope. Clay and concrete roof tile shall be installed on roof slopes in accordance with the recommendations of FRSA/TRI 07320.

R905.3.3.  Underlayment. Required underlayment shall conform with ASTM D 226, Type II; ASTM D 2626 Type II; ASTM D 1970 or ASTM D 6380 Class M and shall be installed in accordance with FRSA/TRI 07320 Manual.

Revise Section R905.3.3.1 to read as follows:

Section R905.3.3.1 Slope and underlayment requirements.

R905.3.3.1  Slope and underlayment requirements.  Refer to FRSA/TRI manual for underlayment and slope requirements for specific roof tile systems.

R905.3.3.2. High slope roofs. Reserved

Section R905.3.3.3 Underlayment and high wind revise text to read as follows:

R905.3.3.3 Underlayment and high wind. Reserved

R905.3.4.  Clay Tile. Clay roof tile shall comply with ASTM C 1167.

Section R905.3.6 Fasteners.  Change to read as shown.

R905.3.6 Fasteners.    Nails shall be corrosion-resistant and not less than 11 gage, 5/16-inch (8.0 mm) head, and of sufficient length to penetrate the deck a minimum of ¾ inch (19.1 mm) or through the thickness of the deck, whichever is less or in accordance with the FRSA/TRI 07320 manual.  Attaching wire for clay or concrete tile shall not be smaller that 0.083 inch (2.1 mm).

R905.3.7 Application. Tile shall be applied in accordance with this chapter and the manufacturer's installation instructions, or recommendations of the FRSA/TRI 07320 based on the following:

Attachment. Clay and concrete roof tiles shall be fastened in accordance with FRSA/TRI Installation Manual 07320.

TABLE R905.3.7  CLAY AND CONCRETE TILE ATTACHMENT

Reserved.

R905.3.7.1.  Hip and ridge tiles.  Hip and ridge tiles shall be installed in accordance with FRSA/TRI 07320 Manual.

R905.3.8 Flashing. At the juncture of roof vertical surfaces, flashing and counter flashing shall be provided in accordance with this chapter and the manufacturer’s installation instructions or recommendations of the FRSA/TRI 07320 Manual.

Overlap with Florida Specific – Roofing TAC

Section R905.4.3 Underlayment.  Change to read as shown. Need to be resolved.

FBC

R905.4.3 Underlayment. Underlayment shall comply with ASTM D 226, Type I or Type II or ASTM D 1970 or ASTM D 4869.

2009 IRC

R905.4.3 Underlayment. Underlayment shall comply with ASTM D 226, Type I or Type II, ASTM D 4869, Type I or Type II, or ASTM D 1970. Underlayment shall be installed in accordance with the manufacturer’s installation instructions.

Staff  recommendation: The IRC09 does cover Florida specific provisions. Recommend using the IRC09 provisions instead of Florida specific provisions.

R905.6.3.1 Ice barrier. Reserved.

Section R905.4.4 Material standards.  Change to read as shown.

R905.4.4 Material standards. Metal roof shingle roof coverings shall comply with Table R905.4.4. The materials used for metal roof shingle roof coverings shall be naturally corrosion resistant or provided with corrosion resistance in accordance with the standards and minimum thicknesses specified in the standards listed in Table R905.4.4.

TABLE R905.10.3(1) METAL ROOF COVERINGS STANDARDS Reserved.

TABLE R905.4.4 METAL ROOF COVERINGS

| ROOF COVERING TYPE | STANDARD | APPLICATION RATE/THICKNESS |
| --- | --- | --- |
| Aluminum | ASTM B 209 | 0.024 inch minimum thickness for roll-formed panels 0.019 inch minimum thickness for press-formed shingles. |
| Aluminum-zinc coated steel | ASTM A 792 | 0.013 inch minimum thickness, AZ 50 (coated minimum application rate) |
| Copper | ASTM B 370 | 16 oz./sq. ft. for metal-sheet roof-covering systems; 12 oz./sq. ft. for preformed metal shingle systems, |
| Galvanized steel | ASTM A 653 | G-90 zinc-coated, 0.013-inch-thick minimum |
| Lead-coated copper | ASTM B 101 |  |
| Hard lead |  | 2 lbs./sq. ft. |
| Soft lead |  | 3 lbs./sq. ft. |
| Prepainted steel | ASTM A 755 | 0.013 inch minimum thickness |
| Terne (tin) and terne-coated stainless |  | Terne coating of 40 lbs. per double base box, field painted where applicable in accordance with manufacturer’s installation instructions. |

For SI:  1 ounce per square foot = 0.0026 kg/m2,

1 pound per square foot = 4.882 kg/m2,

1 inch = 25.4 mm, 1 pound = 0.454 kg.

Section R905.4.5 Application.  Change to read as shown.

R905.4.5  Application.  Metal roof shingles shall be installed in accordance with the approved manufacturer's installation instructions.  The product approval shall state the allowable uplift resistance for the attachment system.  The installation of metal roof shingles shall be limited to roofs where the allowable uplift resistance is equal to or greater than the design uplift pressure for the roof listed in Table R301.2(2).

R905.4.6 Flashing. Roof valley flashing shall be of corrosion-resistant metal of the same material as the roof covering or shall comply with the standards in Table R905.4.4. The valley flashing shall extend at least 8 inches (203 mm) from the center line each way and shall have a splash diverter rib not less than ¾ inch (19.1 mm) high at the flow line formed as part of the flashing. Sections of flashing shall have an end lap of not less than 4 inches (102 mm). The metal valley flashing shall have a 36-inch-wide (914 mm) underlayment directly under it consisting of one layer of underlayment running the full length of the valley, in addition to underlayment required for metal roof shingles.

Section R905.5.3 Underlayment.  Change to read as shown.

R905.5.3 Underlayment. Underlayment shall conform with ASTM D 226, Type I or Type II or ASTM D 1970 or ASTM D 4869.

R905.5.4.  Material standards. Mineral-surfaced roll roofing shall conform to ASTM D 3909 or ASTM D 6380 Class M or Class WS.

Overlap with Florida Specific – Roofing TAC

Change R905.6 as shown:  Need to be resolved.

FBC

R905.6.3  Underlayment. Underlayment shall comply with ASTM D 226, Type II.  Underlayment shall be installed in accordance with the manufacturer’s installation instructions.

R05.6.3.1 Ice barrier. Reserved

2009 IRC

R905.6.3  Underlayment. Underlayment shall comply with ASTM D 226, Type II, or ASTM D 4869, Type I or II..  Underlayment shall be installed in accordance with the manufacturer’s installation instructions.

Staff  recommendation: The IRC09 does cover Florida specific provisions. Recommend using the IRC09 provisions instead of Florida specific provisions.

TABLE R905.6.5

SLATE SHINGLE HEADLAP

| SLOPE | HEADLAP (inches) |
| --- | --- |
| 4:12 ≤ slope < 8:12 | 4 |
| 8:12 ≤ slope < 20:12 | 3 |
| Slope > 20:12 | 2 |

R905.6.6 Flashing. Flashing and counter flashing shall be made with sheet metal. Valley flashing shall be a minimum of 16 inches (406 mm) wide. Valley and flashing metal shall be a minimum thickness as provided in Table R903.1 nonferrous metal or stainless steel.

Section R905.6.7 add to read as shown.

R905.6.7 Slate and slate-type shingles shall be installed in accordance with this chapter and the manufacturer’s installation instructions.  The product approval shall state the allowable uplift resistance for the attachment system.  The installation of slate and slate-type shingles shall be limited to roofs where the allowable uplift resistance is equal to or greater than the design uplift pressure for the roof listed in Table R301.2(2).

Change R905.7 as shown:

R905.7.1.1 Solid sheathing required. Reserved.

R905.7.5  Attachment.  Change to read as shown.

R905.7.5  Attachment.  Attachment in accordance with Table R905.7.5 shall be used for roofs with a mean roof height of 40 feet or less and in regions with a basic wind speed of 100 mph or less.

TABLE R905.7.5

WOOD SHINGLE AND SHAKE INSTALLATION

| ROOF ITEM | WOOD SHINGLES | WOOD SHAKES |
| --- | --- | --- |
| 1. Deck Requirements | Shingles shall be applied to roofs with solid or spaced sheathing. Where spaced sheathing is used, sheathing boards shall not be 4 less than 1" × 4" nominal dimensions and shall be spaced on center equal to the weather exposure to coincide with the placement of fasteners. | Shakes shall be applied to roofs with solid or spaced sheathing. Where spaced sheathing is used, sheathing boards shall not be less than 1" × 4" nominal dimensions and shall be spaced on center equal to the weather exposure to coincide with the placement of fasteners. When 1" × 4" spaced sheathing is installed at 10 inches, boards must be installed between the sheathing boards. |
| 2. Interlayment | No requirements. | Interlayment shall comply with ASTM D 226, Type 1. |
| 3. Underlayment | Underlayment shall comply with ASTM D 226, Type 1. | No requirements. |
| 4. Application | — | — |
| Attachment | Fasteners for wood shingles shall be corrosion resistant with a minimum penetration of ¾ inch into the sheathing. For sheathing less than ½ inch thick, the fasteners shall extend through the sheathing a minimum of ⅜ inch. | Fasteners for wood shakes shall be corrosion resistant with a minimum penetration of ¾ inch into the sheathing. For sheathing less than ½ inch thick, the fasteners shall extend through the sheathing a minimum of ⅜ inch. |
| No. of fasteners | Wood shingles shall be attached to the roof with two fasteners per shingle, positioned no more than 3/4 inch (19.1 mm) from each edge and no more than 1 ½ inch (38.1 mm) above the exposure line. | Wood shakes shall be attached to the roof with two fasteners per shake, positioned no more than 1 inch (25.4 mm) from each edge and no more than 1 ½ inches (38.1 mm) above the exposure line. |

For SI: 1 inch = 25.4 mm

R905.7.6  Attachment for wind speed greater than 100 mph. Wood shingles installed in accordance with Table R905.7.5 and the requirements of R905.7.6 has an allowable uplift resistance of 45 psf.  The installation of wood shingles shall be limited to roofs where the allowable uplift resistance is equal to or greater than the design uplift pressure for the roof listed in Table R301.2(2).

R905.7.6.1  Fasteners.

R905.7.6.1.1  Nails.  Nails to attach the wood shakes shall be 3d stainless steel ring shank nails.  The nails shall have sufficient length to penetrate through the wood shakes and shall penetrate through the sheathing.

R905.7.6.1.2  Screws.  Screws to attach the battens to the framing shall be No. 8 by 2-½ inches (64 mm) long corrosion resistant wood screws.  Wood screws shall be corrosion resistant screws conforming to ANSI/ASME B 18.6.1.  The corrosion resistance shall meet ASTM A 641, Class 1 or an equal corrosion resistance by coating, electro galvanization, mechanical galvanization, stainless steel, nonferrous metal or other suitable corrosion resistant material.

R905.7.6.1.3  Wood battens.  1 x 4 wood battens shall be attached to the wood joists with 2 screws per joist.  The first batten shall be located 6 inches (152 mm) from the outer edge of the wood joist.  Second batten shall be spaced 1-¼ inches (32 mm) from the first batten. The remaining battens shall be spaced a maximum 2 inches (51 mm) apart, except the last one which shall be spaced no greater than ¾ inches (19 mm) from the previous batten.

R905.7.6.1.4  Shingles.  Shingles shall be attached to the battens with 2 nails for each shingle placed 1 1/2 inch  (38 mm) above the exposure line.  The nails shall be ¾ to 1 inch (19 to 25 mm) from the shingle edges.

R905.7.7 [IRC R905.8.6] Application. Wood shingles shall be installed according to this chapter and the manufacturer’s installation instructions. Weather exposure for wood shingles shall not exceed those set in Table R905.7.7.

Section R905.7.8 Flashing revise text to read as follows:

R905.7.8 Flashing.  At the juncture of the roof and vertical surfaces, flashing and counter flashing shall be provided in accordance with the manufacturer’s installation instructions, and where of metal, shall not be less than 0.017-inch (0.48 mm) (No. 26 galvanized sheet gage) corrosion-resistant metal

Section R905.7.8.1 Valley flashing add text to read as follows:

R905.7.8.1 Valley flashing. Roof flashing shall be not less than No. 26 gage [0.017 inches (0.48 mm)] corrosion-resistant sheet metal and shall extend 10 inches (254 mm) from the centerline each way for roofs having slopes less than 12 units vertical in 12 units horizontal (100-percent slope), and 7 inches (178 mm) from the centerline each way for slopes of 12 units vertical in 12 units horizontal and greater. Sections of flashing shall have an end lap of not less than 4 inches (102 mm).

R905.7.8.1.1  Label required. Each bundle of shingles shall be identified by a label of an approved grading or inspection bureau or agency.

Change R905.8 as shown:

R905.8.1.1 Solid sheathing required. Reserved.

R905.8.2  Deck slope. Wood shakes shall only be used on slopes of four (4) units vertical in twelve (12) units horizontal (33-percent slope) or greater.

R905.8.3 Underlayment. Reserved

R905.8.4  Attachment. Attachment in accordance with Table R905.7.5 shall be used for roofs with a mean roof height of 40 feet or less and in regions with a basic wind speed of 100 mph or less.

R905.8.6 Application. Reserved.

R905.8.7  Attachment for wind speed greater than 100 mph.

Wood shakes installed in accordance with Table R905.7.5 and the requirements of R905.8.7 have an allowable uplift resistance of 90 psf.  The installation of wood shakes shall be limited to roofs where the allowable uplift resistance is equal to or greater than the design uplift pressure for the roof listed in Table R301.2(2)

R905.8.7.1  Fasteners.

R905.8.7.1.1  Nails.  Nails to attach the wood shakes shall be 6d stainless steel ring shank nails.  The nails shall have sufficient length to penetrate through the wood shakes and shall penetrate through the sheathing.

R905.8.7.1.2  Screws.  Screws to attach the battens to the framing shall be No. 8 by 2-½ inches long corrosion resistant wood screws.  Wood screws shall be corrosion resistant screws conforming to ANSI/ASME B 18.6.1.  The corrosion resistance shall meet ASTM A 641, Class 1 or an equal corrosion resistance by coating, electro galvanization, mechanical galvanization, stainless steel, nonferrous metal or other suitable corrosion resistant material.

R905.8.7.1.3  Wood battens.  1 x 6 wood battens shall be attached to the wood joists with 2 screws per joist.  The first batten was located 6 inches from the outer edge of the wood joist.  Second batten shall be spaced 1-¼ inches from the first batten. The remaining battens shall be spaced a maximum 2 inches apart, except the last one which shall be spaced no greater than ¾ inches from the previous batten.

R905.8.7.1.4  Shakes.  Shakes shall be attached to the battens with 2 nails for each shake placed 1½ inch above the exposure line.  The nails shall be ¾ to 1 inch from the shake edges.

Overlap with Florida Specific – Structural TAC

Need to be resolved.

FBC

R905.8.8 [IRC R905.8.6]  Application. Wood shakes shall be installed according to this chapter and the manufacturer’s installation instructions. Wood shakes shall be laid with a side lap not less than 1½ inch (38 mm) between joints in adjacent courses. Spacing between shakes in the same course shall be 1/8 inch to 5/8 inch (3.2 mm to 15.9 mm) for shakes and taper sawn shakes of naturally durable wood and shall be ¼ inch to 3/8 inch (6.4 mm to 9.5 mm) for preservative taper sawn shakes. Weather exposure for wood shakes shall not exceed those set forth in Table R905.8.8

TABLE R905.8.8

WOOD SHAKE WEATHER EXPOSURE AND ROOF SLOPE

| ROOFING MATERIAL | LENGTH (inches) | GRADE | EXPOSURE (inches) |
| --- | --- | --- | --- |
|  |  |  | 4:12 pitch or steeper |
| Shakes of naturally durable wood | 18 | No. 1 | 71/2 |
|  | 24 | No. 1 | 10a |
| Preservative-treated taper sawn shakes of Southern Yellow Pine | 18 | No. 1 | 71/2 |
|  | 24 | No. 1 | 10 |
|  | 18 | No. 2 | 51/2 |
|  | 24 | No. 2 | 71/2 |
| Taper-sawn shakes of naturally durable wood | 18 | No. 1 | 71/2 |
|  | 24 | No. 1 | 10 |
|  | 18 | No. 2 | 51/2 |
|  | 24 | No. 2 | 71/2 |

For SI: 1 inch = 25.4 mm.

a. For 24-inch by 3/8-inch handsplit shakes, the maximum exposure is 71/2 inches.

2009 IRC

R905.8.6 Application. Wood shakes shall be installed according to this chapter and the manufacturer’s installation instructions. Wood shakes shall be laid with a side lap not

less than 11/2 inches (38 mm) between joints in adjacent courses. Spacing between shakes in the same course shall be 3/8 inch to 5/8 inch (9.5 mm to 15.9 mm) for shakes and tapersawn shakes of naturally durable wood and shall be 3/8 inch to 5/8 inch (9.5mmto 15.9 mm) for preservative-treated taper sawn shakes.Weather exposure for wood shakes shall not exceed those set forth in Table R905.8.6. Fasteners for wood shakes shall be corrosion-resistant, with a minimum

penetration of 1/2 inch (12.7 mm) into the sheathing. For sheathing less than 1/2 inch (12.7 mm) thick, the fasteners shall extend through the sheathing. Wood shakes shall be attached to the roof with two fasteners per shake, positioned no more than 1 inch (25 mm) from each edge and no more than 2 inches (51 mm) above the exposure line.

Staff  recommendation: The IRC09 does not cover Florida specific provisions. Recommend retaining Florida specific provisions as stated above.

Section R905.8.10 Flashing, add text to read as follows:

R905.8.10  Flashing  At the juncture of the roof and vertical surfaces, flashing and counter flashing shall be provided in accordance with the manufacturer’s installation instructions, and where of metal, shall not be less than 0.017-inch (0.48 mm) (No. 26 galvanized sheet gage) corrosion-resistant metal.

R905.8.10.1  Valley flashing. Valley flashing shall extend at least 11 inches (279 mm) from the centerline each way and have a splash diverter rib not less than 1 inch (25 mm) high at the flow line formed as part of the flashing. Sections of flashing shall have an end lap of not less than 4 inches (102 mm). For roof slopes of four (4) units vertical in twelve (12) units horizontal (33-percent slope) and over, the valley flashing shall have a 36-inch-wide (914 mm) underlayment of one layer of ASTM D 226 Type I underlayment running the full length of the valley, in addition to other required underlayment per Table 903.1  Valley flashing and flashing metal shall be a minimum thickness as provided in Table R903.1 for nonferrous metal or stainless steel.

Add R905.9.2.1 as shown:

R905.9.2.1 Red rosin paper shall be used when the membrane is applied directly to a wood deck or cementitious fiber decks.

Add  R905.10.2.1  as shown:

R905.10.2.1 Underlayment shall be installed as per manufacturer’s installation guidelines.

Section R905.10.3 Material standards.  Change to read as shown.

R905.10.3 Material standards.  Metal-sheet roof covering systems that incorporate supporting structural members shall be designed in accordance with the  Florida Building Code, Building. Metal-sheet roof coverings installed over structural decking shall comply with Table R 905.4.4. The materials used for metal-sheet roof coverings shall be naturally corrosion resistant or provided with corrosion resistance in accordance with the standards and minimum thicknesses shown in Table 905.4.4.

TABLE R905.10.3 METAL ROOF COVERINGS STANDARDS. Reserved..

Overlap with Florida Specific – Roofing TAC

Section R905.10.4 Attachment revise text to read as follows: Need to be resolved

FBC

R905.10.4 Attachment. Metal roof panels shall be secured to the supports in accordance with this chapter and the manufacturer’s installation instructions. Metal roofing fastened directly to steel framing shall be attached by approved fasteners. The following fasteners shall be used:

1. Galvanized fasteners shall be used for galvanized roofs.

2. Hard copper or copper alloy or 300 series stainless steel fasteners shall be used for copper roofs.

3. Stainless steel fasteners are acceptable for all types of metal roofs.

4. Aluminum-zinc coated fasteners are acceptable for aluminum-zinc coated roofs.

2009 IRC

R905.10.4 Attachment. Metal roof panels shall be secured to the supports in accordance with this chapter and the manufacturer’s installation instructions. In the absence of manufacturer’s

installation instructions, the following fasteners shall be used:

1. Galvanized fasteners shall be used for steel roofs.

2. Copper, brass, bronze, copper alloy and Three hundred series stainless steel fasteners shall be used for copper roofs.

3. Stainless steel fasteners are acceptable for metal roofs.

Staff  recommendation: The IRC09 does not cover Florida specific provisions. Recommend retaining Florida specific provisions as stated above.

R905.10.5  Application.  Add text to read as shown.

FBC

R905.10.5  Application. Metal roof panels shall be installed in accordance with this chapter and the manufacturer’s installation instructions.  The installations instruction shall state the allowable uplift resistance for the attachment system.  The installation of metal roof panels shall be limited to roofs where the allowable uplift resistance is equal to or greater than the design uplift pressure for the roof listed in  Table R301.2(2).

Overlap with Florida Specific – Roofing TAC

Need to be resolved.

FBC

R905.10.6 [IRC R 905.10.5] Underlayment. Underlayment shall be installed as per manufacturer’s installation guidelines.

2009 IRC

R905.10.5Underlayment. Underlayment shall be installed in accordance with the manufacturer’s installation instructions.

Staff  recommendation: The IRC09 does cover Florida specific provisions.  Recommend using the IRC09 provisions instead of Florida specific provisions.

Table R905.11.2 Modified Bitumen Roofing Material Standards, revise text to read as follows:

TABLE R905.11.2

MODIFIED BITUMEN ROOFING MATERIAL STANDARDS

| Modified bitumen roof membrane | ASTM D 6162; D 6163; D 6164; D 6222; D 6223; D 6298; D 6509 CGSB 37–56M; |
| --- | --- |

No change to remainder of the table.

Change R905.11.3 as shown:

R905.11.3  Application. Modified bitumen roof shall be installed according to this chapter and the manufacturer’s installation instructions.  The approved allowable uplift resistance for the modified bitumen roof shall be equal to or greater than the uplift resistance for the roof based on Table R301.2(2).

Change R905.12 as shown:

R905.12.3  Application. Thermoset single-ply roof shall be installed according to this chapter and the manufacturer’s installation instructions.  The approved allowable uplift resistance for the thermoset single-ply membrane roof shall be equal to or greater than the uplift resistance for the roof based on Table R301.2(2).

Change R905.13 as shown:

R905.13.3  Application. Thermoplastic single-ply roof shall be installed according to this chapter and the manufacturer’s installation instructions.  The approved allowable uplift resistance for the thermoplastic single-ply roof shall be equal to or greater than the uplift resistance for the roof based on Table R301.2(2).

Change R905.14 as shown:

R905.14.3  Application. Foamed in place roof insulation shall be installed in accordance with this chapter and the manufacturer’s installation instructions. A liquid-applied protective coating that complies with Section R905.15 shall be applied no less than 2 hours nor more than 72 hours following the application of the foam.  The approved allowable uplift resistance for the sprayed polyurethane foam roofing shall be equal to or greater than the uplift resistance for the roof based on Table R301.2(2).

Change R905.15 as shown:

R905.15.3  Application. Liquid-applied roof coatings shall be installed according to this chapter and the manufacturer’s installation instructions.  The approved allowable uplift resistance for the liquid-applied coatings shall be equal to or greater than the uplift resistance for the roof based on Table R301.2(2).

Change Section R907.1 as shown:

R907.1  General. Reroofing shall be done in accordance with the Florida Existing Building Code.

R907.2 Structural and construction loads.  Reserved.

R907.3 Recovering versus replacement.  Reserved.

R907.4 Roof covering.  Reserved.

R907.5 Reinstallation of materials.  Reserved.

R907.6 Flashings.  Reserved.

CHAPTER 10

CHIMNEYS AND FIREPLACES

Change Section R1001.3 and R1001.4 as shown:

R1001.3 Seismic reinforcing.  Reserved.

R1001.3.1 Vertical reinforcing. Reserved,

R1001.3.2 Horizontal reinforcing. Reserved.

R1001.4 Seismic anchorage. Reserved.

R1001.4.1 Anchorage. Reserved.

Change Table R1001.1 as shown “same as the 2007 FBC, Residential”:

TABLE R1001.1

SUMMARY OF REQUIREMENTS FOR MASONRY FIREPLACES AND CHIMNEYS

| ITEM | LETTERa | REQUIREMENTS |
| --- | --- | --- |
| Hearth slab thickness | A | 4″ |
| Hearth extension (each side of opening) | B | 8″ fireplace opening < 6 square foot. 12″ fireplace opening ≥ 6 square foot. |
| Hearth extension (front of opening) | C | 16″ fireplace opening < 6 square foot. 20″ fireplace opening ≥ 6 square foot. |
| Hearth slab reinforcing | D | Reinforced to carry its own weight and all imposed loads. |
| Thickness of wall of firebox | E | 10″ solid brick or 8″ where a firebrick lining is used. Joints in firebrick 1/4 ″ maximum. |
| Distance from top of opening to throat | F | 8″ |
| Smoke chamber wall thickness Unlined walls | G | 6″ 8″ |
| Horizontal reinforcing | J | 1/4 ″ ties at 18″ and two ties at each bend in vertical steel. |
| Bond beams | K | No specified requirements. |
| Fireplace lintel | L | Noncombustible material. |
| Chimney walls with flue lining | M | Solid masonry units or hollow masonry units grouted solid with at least 4 inch nominal thickness. |
| Distances between adjacent flues | — | See Section R1003.13. |
| Effective flue area (based on area of fireplace opening) | P | See Section R1003.15. |
| Clearances: Combustible material Mantel and trim Above roof | R | See Sections R1001.11 and R1003.18. See Section R1001.11, Exception 4. 3′ at roofline and 2′ at 10′. |
| Footing Thickness Width | T | 12″ min. 6″ each side of fireplace wall. |

For SI: 1 inch = 25.4 mm, 1 foot = 304.8 mm, 1 square foot = 0.0929m2.

NOTE: This table provides a summary of major requirements for the construction of masonry chimneys and fireplaces. Letter references are to Figure R1001.1, which shows examples of typical construction. This table does not cover all requirements, nor does it cover all aspects of the indicated requirements. For the actual mandatory requirements of the code, see the indicated section of text.

a. The letters refer to Figure R1001.1.

b. Reserved.

Change Figure R1001.1 as shown:

FIGURE R1001.1

FIREPLACE AND CHIMNEY DETAILS

“same as the 2007 FBC, Residential”

Brick Firebox and Chimney – Sectional Side View on Wood Floor

[Delete H, Vertical reinforcing and J, Horizontal reinforcing ties.]

Change R1001.12 as shown:

R1001.12 Fireplace fireblocking. Fireplace fireblocking shall comply with the provisions of Section R602.1.2.

Change R1002.4 as shown:

R1002.4 Seismic reinforcing.  Reserved.

Change R1003.3 as shown:

R1003.3 Seismic reinforcing. Reserved.

R1003.3.1 Vertical reinforcing. Reserved.

R1003.3.2 Horizontal reinforcing. Reserved.

Change R1003.4 as shown:

R1003.4 Seismic anchorage. Reserved.

R1003.4.1 Anchorage. Reserved.

CHAPTER 11

ENERGY EFFICIENCY

Add text to read from the 2007 Florida Building Code, Residential.

Part V - Mechanical

Chapter 12, Mechanical Administration

Section M1202 Existing Mechanical Systems

M1202.1 Additions, alterations or repairs.  Change to read as shown:

M1202.1 Additions, alterations or repairs. See The Florida Building Code, Existing Building.

M1202.2  Existing installations.  Change to read as shown.

M1202.2  Existing installations.  Reserved.

M1202.3 Maintenance.  Change to read as shown.

M1202.3 Maintenance.  Reserved.

Chapter 13, General Mechanical System Requirements

Section M1301 General

M1301.1 Scope.  Change to read as shown.

M1301.1 Scope. The provisions of this chapter shall govern the installation of mechanical systems not specifically covered in other chapters applicable to mechanical systems. Installations of mechanical appliances, equipment and systems not addressed by this code shall comply with the applicable provisions of the Florida Building Code, Mechanical and the Florida Building Code, Fuel Gas.

Overlap with Florida Specific – Mechanical TAC

Section M1305 Appliance Access.  Need to be resolved.

2009 IRC

M1305.1.1 Furnaces and air handlers. Furnaces and air handlers within compartments or alcoves shall have a minimum working space clearance of 3 inches (76 mm) along the sides, back and top with a total width of the enclosing space being at least 12 inches (305 mm) wider than the furnace or air handler. Furnaces having a firebox open to the atmosphere shall have at least a 6-inch (152 mm) working space along the front combustion chamber side. Combustion

air openings at the rear or side of the compartment shall comply with the requirements of Chapter 17.

Exception: This section shall not apply to replacement appliances installed in existing compartments and alcoves where the working space clearances are in accordance with the equipment or appliance manufacturer’s installation instructions.

[Possible conflict with Section M1601.3.3, FL specific.]

Staff recommendation: No conflict exists.

Overlap with Florida Specific – Mechanical TAC

M1305.1.3 Appliances in attics.  Change to read as shown. Need to be resolved.

FBC

M1305.1.3 Appliances in attics.  Attics containing appliances requiring access shall be provided with an opening and unobstructed passageway large enough to allow removal of the largest appliance. The passageway shall not be less than 30 inches (762 mm) high and 22 inches (559 mm) wide and not more than 6 feet (1829 mm) in length measured along the centerline of the passageway from the attic access opening to the appliance’s service panel. The passageway shall have continuous solid flooring not less than 24 inches (610 mm) wide. A level service space not less than 30 inches (762 mm) deep and 30 inches (762 mm) wide shall be present at the front or service side of the appliance. The clear access opening dimensions shall be a minimum of 20 inches by 30 inches (508 mm by 762 mm), where such dimensions are large enough to allow removal of the largest appliance.

Exception: The passageway and level service space are not required where the appliance is capable of being serviced and removed through the required opening.

2009 IRC

M1305.1.3 Appliances in attics. Attics containing appliances shall be provided with an opening and a clear and unobstructed passageway large enough to allow removal of the largest appliance, but not less than 30 inches (762 mm) high and 22 inches (559 mm) wide and not more than 20 feet (6096 mm) long measured along the centerline of the passageway from the opening to the appliance. The passageway shall have continuous solid flooring in accordance with Chapter 5 not less than 24 inches (610 mm) wide. A level service space at least 30 inches (762 mm) deep and 30 inches (762 mm) wide shall be present along all sides of the appliance where access is required. The clear access opening dimensions shall be a minimum of 20 inches by 30 inches (508 mm by 762 mm), and large enough to allow removal of the largest appliance.

Exceptions:

1. The passageway and level service space are not required where the appliance can be serviced and removed through the required opening.

2. Where the passageway is unobstructed and not less than 6 feet (1829 mm) high and 22 inches (559 mm) wide for its entire length, the passageway shall be not more than 50 feet (15 250 mm) long.

Staff recommendation:  Florida specific provisions are not covered by the IRC09.  Consider using the IMC09 provisions as the base text and revise to add Florida specific provisions.

M1305.1.3.1 Electrical requirements.  Change to read as shown.

M1305.1.3.1 Electrical requirements. A luminaire controlled by a switch located at the required passageway opening and a receptacle outlet shall be installed at or near the appliance location in accordance with Chapter 34.

M1305.1.3.2 Air-handling units.  Add to read as shown.

M1305.1.3.2 Air-handling units.  Air-handling units shall be allowed in attics if the following conditions are met:

1.The service panel of the equipment is located within 6 feet (1829 mm) of an attic access.

2.A device is installed to alert the owner or shut the unit down when the condensation drain is not working properly.

3.The attic access opening is of sufficient size to replace the air handler.

4.A notice is posted on the electric service panel indicating to the homeowner that the air handler is located in the attic. Said notice shall be in all capitals, in 16 point type, with the title and first paragraph in bold:

##### NOTICE TO HOMEOWNER

A PART OF YOUR AIR CONDITIONING SYSTEM, THE

AIR HANDLER, IS LOCATED IN THE ATTIC. FOR PROPER, EFFICIENT, AND ECONOMIC OPERATION OF THE AIR CONDITIONING SYSTEM, YOU MUST ENSURE THAT REGULAR MAINTENANCE IS PERFORMED. YOUR AIR CONDITIONING SYSTEM IS EQUIPPED WITH ONE OR BOTH OF THE FOLLOWING:

1) A DEVICE THAT WILL ALERT YOU WHEN THE CONDENSATION DRAIN IS NOT WORKING PROPERLY OR

2) A DEVICE THAT WILL SHUT THE SYSTEM DOWN WHEN THE CONDENSATION DRAIN IS NOT WORKING. TO LIMIT POTENTIAL DAMAGE TO YOUR HOME, AND TO AVOID DISRUPTION OF SERVICE, IT IS RECOMMENDED THAT YOU ENSURE PROPER WORKING ORDER OF THESE DEVICES BEFORE EACH SEASON OF PEAK OPERATION.

Overlap with Florida Specific – Mechanical TA

M1305.1.4.1 Clearances from grade.  Change to read as shown. Need to be resolved.

4FBC

M1305.1.4.1 Clearances from grade.  Equipment and appliances installed at grade level shall be supported on a level minimum 3½-inch (89 mm) concrete slab or other approved material extending a minimum of 2 inches (51 mm) above adjoining finished grade. Suspended equipment and appliances shall be installed a minimum of 6 inches (152 mm) above adjoining grade to provide support and protection from contact with soil or water.

Exception: On changeouts or new installations of existing buildings where equipment is replaced that has a support platform approved under a previous code.

2009 IRC

M1305.1.4.1 Ground clearance. Equipment and appliances supported from the ground shall be level and firmly supported on a concrete slab or other approved material extending not less than 3 inches ( 76mm) above the adjoining ground. Such support shall be in accordance with the manufacturer’s installation instructions. Appliances suspended from the floor shall have a clearance of not less than 6 inches (152 mm) from the ground.

Staff recommendation:  Florida specific provisions are more specific than those of IRC09.  Consider continue using Florida specific provisions.

Section M1307 Appliance Installation

M1307.2 Anchorage of appliances.  Change to read as shown.

M1307.2 Anchorage of appliances.  Appliances designed to be fixed in position shall be fastened or anchored in an approved manner. In Seismic Design Categories D1 and D2, water heaters shall be anchored or strapped to resist horizontal displacement caused by earthquake motion. Strapping shall be at points within the upper one-third and lower one-third of the appliance’s vertical dimensions. At the lower point, the strapping shall maintain a minimum distance of 4 inches (102 mm) above the controls.

Add M1307.2.1 Wind resistance to read as follows:

M1307.2.1 3 Wind resistance.  Mechanical equipment, appliances and supports that are exposed to wind shall be designed and installed to resist the wind pressures on the equipment and the supports as determined in accordance with the Florida Building Code, Building.

M1307.3 Elevation of ignition source. Reserved.

M1307.5 Electrical appliances.  Change to read as shown.

M1307.5 Electrical appliances. Electrical appliances shall be installed in accordance with Chapter 34 of this code.

Section M1308 Mechanical Systems Installation

M1308.1 Drilling and notching.  Change to read as shown.

M1308.1 Drilling and notching. Wood-framed structural members shall be drilled, notched or altered in accordance with the provisions of Sections R502.2.7, R602.2.7, R602.267.1 and R802.2.6. Holes in load-bearing members of cold-formed steel light-frame construction shall be permitted only in accordance with Sections R505.2.5, R603.2.5 and R804.2.5. In accordance with the provisions of Sections R505.3.5, R603.3.4 and R804.3.4, cutting and notching of flanges and lips of load-bearing members of cold-formed steel light frame construction shall not be permitted. Structural insulated panels (SIPs) shall be drilled and notched or altered in accordance with the provisions of Section R612.9.

Chapter 14, Heating and Cooling Equipment

Section M1401 General

Section M1405 Baseboard Convectors

M1405.1 General.  Change to read as shown.

M1405.1 General. Electric baseboard convectors shall be installed in accordance with the manufacturer’s installation instructions and Chapter 34 of this code.

Section M1406 Radiant Heating Systems

M1406.1 General.  Change to read as shown.

M1406.1 General. Electric radiant heating systems shall be installed in accordance with the manufacturer’s installation instructions and Chapter 34 of this code.

M1406.2 Clearances.  Change to read as shown.

M1406.2 Clearances. Clearances for radiant heating panels or elements to any wiring, outlet boxes and junction boxes used for installing electrical devices or mounting luminaires shall comply with Chapter 34 of this code.

Section M1407 Duct Heaters

M1407.1 General.  Change to read as shown.

M1407.1 General. Electric duct heaters shall be installed in accordance with the manufacturer’s installation instructions and Chapter 34 of this code. Electric furnaces shall be tested in accordance with UL 1995.

Overlap with Florida Specific – Mechanical TAC

Section M1411.3.1 Auxiliary and secondary drain systems revise text to read as follows:

[IRC text has been revised. Consider potential conflicts.] Need to be resolved.

M1411.3.1 Auxiliary and secondary drain systems. In addition to the requirements of Section M1411.3, a secondary drain or auxiliary drain pan shall be required for each cooling or evaporator coil where damage to any building components will occur as a result of overflow from the equipment drain pan or stoppage in the condensate drain piping. Such piping shall maintain a minimum horizontal slope in the direction of discharge of not less than 1/8 unit vertical in 12 units horizontal (1-percent slope). Drain piping shall be a minimum of 3/4-inch (19 mm) nominal pipe size. One of the following methods shall be used:

1. An auxiliary drain pan with a separate drain shall be installed under the coils on which condensation will occur. The auxiliary pan drain shall discharge to a conspicuous point of disposal to alert occupants in the event of a stoppage of the primary drain. The pan shall have a minimum depth of 1.5 inches (38 mm), shall not be less than 3 inches (76 mm) larger than the unit or the coil dimensions in width and length and shall be constructed of corrosion-resistant material. Metallic pans shall have a minimum thickness of not less than 0.0276-inch (0.7 mm) galvanized sheet metal. Nonmetallic pans shall have a minimum thickness of not less than 0.0625 inch (1.6 mm).

2009 IRC

1. An auxiliary drain pan with a separate drain shall be installed under the coils on which condensation will occur. The auxiliary pan drain shall discharge to a conspicuous point of disposal to alert occupants in the event of a stoppage of the primary drain. The pan shall have a minimum depth of 1.5 inches (38 mm), shall not be less than 3 inches (76 mm) larger than the unit or the coil dimensions in width and length and shall be constructed of corrosion-resistant material. Galvanized sheet steel pans shall have a minimum thickness of not less than 0.0236-inch (0.6010 mm) (No. 24 Gage). Nonmetallic pans shall have a minimum thickness of not less than 0.0625 inch (1.6 mm).

FBC

2. A separate overflow drain line shall be connected to the drain pan provided with the equipment. This overflow drain shall discharge to a conspicuous point of disposal to alert occupants in the event of a stoppage of the primary drain. The overflow drain line shall connect to the drain pan at a higher level than the primary drain connection. As an alternative to a separate drain line, a water-level detection device that will shut off the equipment served prior to overflow of the pan shall be provided. The water-level detection device shall connect to the drain pan at a higher level than the primary drain connection.

3. An auxiliary drain pan without a separate drain line shall be installed under the coils on which condensate will occur. This pan shall be equipped with a water level detection device conforming to UL 508 that will shut off the equipment served prior to overflow of the pan. The auxiliary drain pan shall be constructed in accordance with Item 1 of this section.

2009 IRC

3. An auxiliary drain pan without a separate drain line shall be installed under the coils on which condensation will occur. This pan shall be equipped with a water level detection device conforming to UL 508 that will shut off the equipment served prior to overflow of the pan. The pan shall be equipped with a fitting to allow for drainage. The auxiliary drain pan shall be constructed in accordance with Item 1 of this section.

FBC

4. Reserved.

2009 IRC

4. A water level detection device conforming to UL 508 shall be installed that will shut off the equipment served in the event that the primary drain is blocked. The device shall be installed in the primary drain line, the overflow drain line or the equipment-supplied drain pan, located at a point higher than the primary drain line connection and below the overflow rim of such pan.  [There is no change to this subsection.]

M1411.3.1.1 Water-level monitoring devices. On down-flow units and all other coils that have no secondary drain or provisions to install a secondary or auxiliary drain pan, a water-level monitoring device shall be installed inside the primary drain pan. This device shall shut off the equipment served in the event that the primary drain becomes restricted. Devices shall not be installed in the drain line.

Staff recommendation:  Florida specific provisions are not covered by the IMC09.  Consider using the IMC09 provisions as the base text and revise to add into it Florida specific provisions.

Chapter 15, Exhaust systems

Overlap with Florida Specific – Mechanical TAC

Section M1502.6 Duct length add text to read as follows: Need to be resolved.

FBC

M1502.6 Duct length. The maximum length of a clothes dryer exhaust duct shall not exceed 25 feet (7620 mm) from the dryer location to the wall or roof termination. The maximum length of the duct shall be reduced 2.5 feet (762 mm) for each 45-degree (0.8 rad) bend and 5 feet (1524 mm) for each 90-degree (1.6 rad) bend. The maximum length of the exhaust duct does not include the transition duct.

Exceptions:

1. Where a clothes dryer booster fan is installed and listed and labeled for the application, the maximum length of the exhaust duct, including any transition duct, shall be permitted to be in accordance with the booster fan manufacturer’s installation instructions. Where a clothes dryer booster fan is installed and not readily accessible from the room in which the dryer is located, a permanent identifying label shall be placed adjacent to where the exhaust duct enters the wall. The label shall bear the words “This dryer exhaust system is equipped with a remotely located booster fan.”

2. Where the make and model of the clothes dryer to be installed is known and the manufacturer’s installation instructions for the dryer are provided to the building official, the maximum length of the exhaust duct, including any transition duct, shall be permitted to be in accordance with the dryer manufacturer’s installation instructions.

3. Where large-radius 45-degree (0.8 rad) and 90-degree (1.6 rad) bends are installed, determination of the equivalent length of clothes dryer exhaust duct for each bend by engineering calculation in accordance with the ASHRAE Fundamentals Handbook shall be permitted.

[M1502.4.4 of the IRC has been changed as follows. Consider potential conflicts.]

IRC

M1502.4.4 Duct length. The maximum allowable exhaust duct length shall be determined by one of the methods specified in Section M1502.4.4.1 or M1502.4.4.2.

M1502.4.4.1 Specified length. The maximum length of the exhaust duct shall be 25 feet (7620 mm)from the connection to the transition duct from the dryer to the outlet terminal. Where fittings are used, the maximum length of the exhaust duct shall be reduced in accordance with Table M1502.4.4.1.

M1502.4.4.2 Manufacturer’s instructions. The size and maximum length of the exhaust duct shall be determined by the dryer manufacturer’s installation instructions. The code official shall be provided with a copy of the installation instructions for the make and model of the dryer at the concealment inspection. In the absence of fitting equivalent length calculations from the clothes dryer manufacturer, Table M1502.4.4.1 shall be used.

TABLE M1502.4.4.1

DRYER EXHAUST DUCT FITTING EQUIVALENT LENGTH

DRYER EXHAUST DUCT FITTING TYPE EQUIVALENT LENGTH

| 4 inch radius mitered 45 degree elbow | 2 feet 6 inches |
| --- | --- |
| 4 inch radius mitered 90 degree elbow | 5 feet |
| 6 inch radius smooth 45 degree elbow | 1 foot |
| 6 inch radius smooth 90 degree elbow | 1 foot 9 inches |
| 8 inch radius smooth 45 degree elbow | 1 foot |
| 8 inch radius smooth 90 degree elbow | 1 foot 7 inches |
| 10 inch radius smooth 45 degree elbow | 9 inches |
| 10 inch radius smooth 90 degree elbow | 1 foot 6 inches |

For SI: 1 inch = 25.4 mm, 1 foot = 304.8 mm, 1 degree = 0.0175 rad.

Staff recommendation:  Florida specific provisions are not covered by the IMC09.  Consider using the IMC09 provisions as the base text and revise to add into it Florida specific provisions.

Chapter 16, Duct Systems

Section M1601 Duct Construction.

M1601.1 Duct design.  Duct systems serving heating, cooling and ventilation equipment shall be fabricated in accordance with the provisions of this section and ACCA Manual D or other approved methods.

Overlap with Florida Specific – Mechanical TAC

IRC M1601.1.1 is changed. Consider potential conflicts.

FBC

M1601.1.1 Duct insulation. See Section N1110.ABC.2 for duct insulation requirements.

M1601.1.1 Above-ground duct systems. Above-ground duct systems shall conform to the following:

[No change to 1.]

M1601.4 Duct classification.

2. Ducts shall be classified based on the maximum operating pressure of the duct at pressures of positive or negative 0.5, 1.0, 2.0, 3.0, 4.0, 6.0 or 10.0 inches of water column. The pressure classifications of ducts shall equal or exceed the design pressure of the air distribution in which the ducts are utilized. Factory-made air ducts shall be constructed of Class 0 or Class 1 materials as designated in Table M1601.1.1(1) M1601.4.

[No change to 3 – 7.]

TABLE M1601.1.1(1) .4

CLASSIFICATION OF FACTORY-MADE AIR DUCTS

| DUCT CLASS | MAXIMUM FLAME-SPREAD RATING |
| --- | --- |
| 0 1 | 0 25 |

IRC Table M1601.1.1(2) [FL Table M1601.5], Gages of Metal Ducts and Plenums Used for Heating or Cooling, has been revised as shown. Consider potential conflicts. Recommend return FL Table M1601.5 to Section M1601.1.

TABLE M1601.1.1(2) M1601.5

GAGES OF METAL DUCTS AND PLENUMS USED FOR HEATING OR COOLING

| TYPE OF DUCT | SIZE (inches) | MINIMUM THICKNESS (inch) | EQUIVALENT GALVANIZED SHEET GAGE | APPROXIMATE ALUMINUM B & S GAGE |
| --- | --- | --- | --- | --- |
| Round ducts and enclosed rectangular ducts | 14 or less over 14 | 0.013 0.016 | 30 28 | 26 24 |
| Exposed rectangular ducts | 14 or less over 14 | 0.016 0.019 | 28 26 | 24 22 |

For SI:	1 inch = 25.4 mm.

2009 IRC

| DUCT SIZE | MINIMUM THICKNESS (inches) | EQUIVALENT GALVANIZED SHEET No. | MINIMUM THICKNESS (inches) |
| --- | --- | --- | --- |
| Round ducts and enclosed rectangular ducts 14 inches or less 16 and 18 inches 20 inches and over | 0.0157 0.0187 0.0236 | 28 26 24 | 0.0175 0.018 0.023 |
| Exposed rectangular ducts 14 inches or Over 14 inches | 0.0157 0.0187 | 28 26 | 0.0175 0.018 |

For SI: 1 inch = 25.4 mm.

a. For duct gages and reinforcement requirements at static pressures of 1/2 inch, 1 inch and 2 inches  w.g., SMACNADuct Construction Standard, Tables 2-1; 2-2 and 2-3 shall apply.

Staff recommendation:  Recommend move Florida-specific language in M1601.1.1 to M1601.3 and return IRC language for Above-ground duct systems as shown. Return FL M1601.4 back to M1601.1.1 #2.

M1601.1.2 Underground duct systems. [No change]

M1601.2 Factory-made ducts.  Delete and replace to read as follows.

M1601.2 Flexible air ducts and flexible air connectors, general. Flexible air ducts, both metallic and nonmetallic, shall comply with Sections M1601.2.1, M1601.2.2, M1601.2.5 and M1601.2.7. Flexible air connectors, both metallic and nonmetallic, shall comply with Sections M1601.2.3 through M1601.2.7.

M1601.2.1 Flexible air ducts. Flexible air ducts, both metallic and nonmetallic, shall be tested in accordance with UL 181. Such ducts shall be listed and labeled as Class 0 or Class 1 flexible air ducts and shall be installed in accordance with Section M1307.

M1601.2.2 Duct length. Flexible air ducts shall not be limited in length.

M1601.2.3 Flexible air connectors. Flexible air connectors, both metallic and nonmetallic, shall be tested in accordance with UL181. Such connectors shall be listed and labeled as Class 0 or Class 1 flexible air connectors and shall be installed in accordance with Section M1307.

M1601.2.4 Connector length. Flexible air connectors shall be limited in length to 14 feet (4267 mm).

M1601.2.5 Air temperature. The design temperature of air to be conveyed in flexible air ducts and flexible air connectors shall be less than 250°F (121°C).

M1601.2.6 Flexible air duct and air connector clearance. Flexible air ducts and air connectors shall be installed with a minimum clearance to an appliance as specified in the appliance manufacturer’s installation instructions.

M1601.2.7 Penetrations prohibited. Flexible air ducts and flexible air connectors shall not pass through any fire-resistance-rated assembly. Flexible air connectors shall not pass through any wall, floor or ceiling.

M1601.3 Duct insulation materials. IRC M1601.1.1. Consider potential conflicts.  Recommend add Florida-specific language from Section M1601.1.1 to M1601.3 as shown.

M1601.3 Duct insulation materials. [from FL M1601.1.1] See Section 403.2.1 of the Florida Building Code, Energy Conservation, for duct insulation R-value requirements.

Duct insulation materials shall conform to the following requirements:

[No change to 1. – 3.]

Overlap with Florida Specific – Mechanical TAC

M1601.4.1 of the IRC has been changed. Consider potential conflicts.

M1601.4 Installation.  Replace to read as shown.

M1601.4 Duct installation. An air distribution system shall be designed and installed to supply the required distribution of air. The installation of an air distribution system shall not affect the fire protection requirements specified in the building code. Ducts shall be constructed, braced, reinforced and installed to provide structural strength and durability in accordance with Table M1601.4 [see explanatory note at M1601.5]. All transverse joints, longitudinal seams and fitting connections shall be securely fastened and sealed in accordance with the applicable standards of this section.

All enclosures which form the primary air containment passageways for air distribution systems shall be considered ducts or plenum chambers and shall be constructed and sealed in accordance with the applicable criteria of this section.

M1601.4.1 Duct installation, general.

M1601.4.1.1 Mechanical fastening. All joints between sections of air ducts and plenums, between intermediate and terminal fittings and other components of air distribution systems, and between subsections of these components shall be mechanically fastened to secure the sections independently of the closure system(s). Where a duct connection is made that is partially inaccessible, three screws or rivets shall be equally spaced on the exposed portion of the joint so as to prevent a hinge effect.

M1601.4.1.2 Sealing. Air distribution system components shall be sealed with approved closure systems.

M1601.4.1.3 Space provided. Sufficient space shall be provided adjacent to all mechanical components located in or forming a part of the air distribution system to assure adequate access for (1) construction and sealing in accordance with the requirements of Section M1601.3 of this code; (2) inspection; and (3) cleaning and maintenance. A minimum of 4 inches (102 mm) is considered sufficient space around air handling units.

Exception: Retrofit or replacement units not part of a renovation are exempt from the minimum clearance requirement.

M1601.4.1.4 Product application. Closure products shall be applied to the air barriers of air distribution system components being joined in order to form a continuous barrier or they may be applied in accordance with the manufacturer’s instructions or appropriate industry installation standard where more restrictive.

M1601.4.1.5 Surface preparation. The surfaces upon which closure products are to be applied shall be clean and dry in accordance with the manufacturer’s installation instructions.

M1601.4.1.6 Approved mechanical attachments. Approved mechanical attachments for air distribution system components include screws, rivets, welds, interlocking joints crimped and rolled, staples, twist in (screw attachment), and compression systems created by bend tabs or screw tabs and flanges or by clinching straps. Mechanical attachments shall be selected to be appropriate to the duct system type.

M1601.4.1.7 Approved closure systems. Closure system materials, including adhesives when used, shall have a flame spread rating not over 25 without evidence of continued progressive combustion and a smoke developed rating not over 50 when tested in accordance with the ASTM E 84. The following closure systems and materials are approved for air distribution construction and sealing for the applications and pressure classes prescribed in [Sections M1601.4. through Sections M1601.4.11] OR [in Table M1601.4.1:

1.	Metal closures.

a. Welds applied continuously along metal seams or joints through which air could leak.

b. Snaplock seams, and grooved, standing, double-corner, and Pittsburgh-lock seams as defined by SMACNA, as well as all other rolled mechanical seams. All seams shall be rolled or crimped.

2.	Gasketing, which achieves a 25/50 flame spread, smoke density development rating under ASTM E 84 or UL 723, provided that it is used only between mated surfaces which are mechanically fastened with sufficient force to compress the gasket and to fill all voids and cracks through which air leakage would otherwise occur.

3.	Mastic closures. Mastic shall be placed over the entire joint between mated surfaces. Mastics shall not be diluted. Approved mastics include the following:

a. Mastic or mastic plus embedded fabric systems applied to fibrous glass ductboard that are listed and labeled in accordance with UL 181A, Part III.

b. Mastic or mastic plus embedded fabric systems applied to nonmetal flexible duct that are listed and labeled in accordance with the 181B, Part II.

c. Mastic ribbons, which achieve a 25/50 flame spread, smoke density development rating under ASTM E 84 or UL 723, provided that they may be used only in flange-joints and lap-joints, such that the mastic resides between two parallel surfaces of the air barrier and that those surfaces are mechanically fastened.

4.	Tapes. Tapes shall be applied such that they extend not less than 1 inch (25 mm) onto each of the mated surfaces and shall totally cover the joint. When used on rectangular ducts, tapes shall be used only on joints between parallel rigid surfaces and on right angle joints. Approved tapes include the following:

a.	Pressure-sensitive tapes.

1)	Pressure-sensitive tapes applied to fibrous glass ductboard that are listed and labeled in accordance with UL 181A, Part I.

2)	Pressure-sensitive tapes applied to nonmetal flexible duct that are listed and labeled in accordance with UL 181B, Part I.

b.	Heat-activated tapes applied to fibrous glass ductboard that are listed and labeled in accordance with UL 181A, Part II.

5.	Aerosol sealant. Such sealants shall be installed by manufacturer-certified installers following manufacturer instructions and shall achieve 25/50 flame spread/smoke density development ratings under ASTM E 84 or UL 723.

6.  Polyurethane foam. Spray polyurethane foam shall be permitted to be applied without additional joint seals.

IRC M1601.4.1 has been changed. Resolve potential conflicts.

M1601.4.1 Joints and seams. Joints of duct systems shall be made substantially airtight by means of tapes, mastics, liquid sealants, gasketing or other approved closure systems. Closure systems used with rigid fibrous glass ducts shall comply with UL181A and shall be marked 181A-P for pressure-sensitive tape, 181A-M for mastic or 181 A-H for heat-sensitive tape. Closure systems used with flexible air ducts and flexible air connectors shall comply with UL 181B and shall be marked 181B-FX for pressure-sensitive tape or 181B-M for mastic. Duct connections to flanges of air distribution system equipment or sheet metal fittings shall be mechanically fastened. Mechanical fasteners for use with flexible nonmetallic air ducts shall comply with UL 181B and shall be marked 181B-C. Crimp joints for round metal ducts shall have a contact lap of at least 11/2inches (38 mm) and shall be mechanically fastened by means of at least three sheet-metal screws or rivets equally spaced around the joint. Closure systems used to seal metal ductwork shall be installed in accordance with the manufacturer’s installation instructions.

Exceptions:

1. Spray polyurethane foam shall be permitted to be applied without additional joint seals.

2. Where a duct connection is made that is partially inaccessible, three screws or rivets shall be equally spaced on the exposed portion of the joint so as to prevent a hinge effect.

3. Continuously welded and locking type longitudinal joints and seams in ducts operating at static pressures less than 2 inches of water column (500 Pa) pressure classification shall not require additional closure systems.

Staff recommendation:  Florida specific provisions are not covered by the IRC09.  Consider continue using Florida specific provisions.

M1601.4.2 Reserved. Plastic duct joints. Joints between plastic ducts and plastic fittings shall be made in accordance with the manufacturer’s installation instructions. [Rationale: Plastic ducts should be included with other ducts]

M1601.4.3 Support.

M1601.4.3.1 Metal ducts. Metal ducts shall be supported by 1/2-inch (13 mm) wide 18-gage metal straps or 12-gage galvanized wire at intervals not exceeding 10 feet (3048 mm) or other approved means. Nonmetallic ducts shall be supported in accordance with the manufacturer’s installation instructions.

M1601.4.3.2 6.3.6 Flexible duct installation and support. Flexible ducts shall be configured and supported so as to prevent the use of excess duct material, prevent duct dislocation or damage, and prevent constriction of the duct below the rated duct diameter in accordance with the following requirements:

1.	Ducts shall be installed fully extended. The total extended length of duct material shall not exceed 5 percent of the minimum required length for that run.

2.	Bends shall maintain a center line radius of not less than one duct diameter.

3.	Terminal devices shall be supported independently of the flexible duct.

4.	 Horizontal duct shall be supported at intervals not greater than 5 feet (1524 mm). Duct sag between supports shall not exceed 1/2 inch (12.7 mm) per foot of length. Supports shall be provided within 1½ feet (457 mm) of intermediate fittings and between intermediate fittings and bends. Ceiling joists and rigid duct or equipment may be considered to be supports.

5.	Vertical duct shall be stabilized with support straps at intervals not greater than 6 feet (1829 mm).

6.	Hangers, saddles and other supports shall meet the duct manufacturer’s recommendations and shall be of sufficient width to prevent restriction of the internal duct diameter. In no case shall the material supporting flexible duct that is in direct contact with it be less than 1½ inches (38 mm) wide.

Mechanical TAC

Staff recommendation:  Move FL M1601.4 back to M1601.1.1#2.

M1601.4 Duct classification. Ducts shall be classified based on the maximum operating pressure of the ducvt at pressures of positive or negative 0.5, 1.0, 2.0, 3.0, 4.0 6.0 or 10.0 inches of water column.  The pressure classification of ducts shall equal or exceed the design pressure of the air distribution in which the ducts are utilized.

M1601.4.1 through M1601.4.5 Reserved.

M1601.4.4 Fireblocking. Duct installations shall be fireblocked in accordance with Section R602.8.

M1601.4.5 Duct insulation installation. Duct insulation shall be installed in accordance with the following requirements:

1. A vapor retarder having a maximum permeance of 0.05 perm [2.87 ng/(s m2 Pa)] in accordance with ASTM E 96, or aluminum foil with a minimum thickness of 2 mils (0.05 mm), shall be installed on the exterior of insulation on cooling supply ducts that pass through unconditioned spaces conducive to condensation except where the insulation is spray polyurethane foam with a maximum water vapor permeance of 3 perm per inch [1722 ng/(s ·m2 ·Pa)] at the installed thickness.

2. Exterior duct systems shall be protected against the elements.

3. Duct coverings shall not penetrate a fireblocked wall or floor.

M1601.4.6 Factory-made air ducts.

M1601.4.6.1 Prohibited locations. Factory-made air ducts shall not be installed in or on the ground, in tile or metal pipe, or within masonry or concrete.

M1601.4.6.2 [IRC M1601.2.1] Vibration isolators. Vibration isolators installed between mechanical equipment and metal ducts shall be fabricated from approved materials and shall not exceed 10 inches (254 mm) in length.

M1601.4.7 Duct separation. Ducts shall be installed with at least 4 inches (102 mm) separation from earth except where they meet the requirements of Section M1601.1.2.

M1601.4.8 Ducts located in garages. Ducts in garages shall comply with the requirements of Section R302.5.2.

M1601.4.9 [FL M1601.3.8] Flood hazard areas.  In areas prone to flooding as established by Table R301.2(1), duct systems shall be located or installed in accordance with Section R322.1.6.See Section R323.

M1601.4.10 9  Condensation. Provisions shall be made to prevent the formation of condensation on the exterior of any duct.

M1601.4.10 Location. Ducts shall not be installed in or within 4 inches (102 mm) of the earth, except where such ducts comply with Section M1601.4.8.

M1601.4.11 Mechanical protection. Ducts installed in locations where they are exposed to mechanical damage by vehicles or from other causes shall be protected by approved barriers.

M1601.4.12  Weather protection. All ducts including linings, coverings and vibration isolation connectors installed on the exterior of the building shall be adequately protected against the elements.

M1601.4.13 Registers, grilles and diffusers. Duct registers, grilles and diffusers shall be installed in accordance with the manufacturer’s installation instructions, and shall have a flame spread rating not over 25 without evidence of continued progressive combustion and a smoke-developed rating not over 50 when tested in accordance with ASTM E 84. Balancing dampers or other means of supply air adjustment shall be provided in the branch ducts or at each individual duct register, grille or diffuser.

Mechanical TAC

M1601.5 Under-floor plenums. Move to M1601.12. Delete and replace to read as shown.

OR consolidate FL M1601.5 – M1601.11 into Table M1601.4 (should not use table.  Using table is a code change) and reference from M1601.4.  Add Table M1601.4 as shown and leave Under-floor plenums as M1601.5.

M1601.5 Metallic ducts, rigid and flexible. All ducts shall be constructed of iron, steel, aluminum or other approved material. Ducts shall be constructed as specified in the SMACNA HVAC Duct Construction Standards—Metal and Flexible.

Exception: Ducts installed within single dwelling units shall have a minimum thickness as specified in Table M1601.5.

All transverse joints, longitudinal seams and duct wall penetration of ducts and joints with other air distribution systems components shall be mechanically attached and sealed using approved closure systems for that pressure class specified in Section M1601.5.1 or M1601.5.2.

M1601.5.1 Pressure less than 1-inch water gage, approved closure systems. The following closure systems are approved for rigid metal duct designed to be operated at pressures less than 1 inch water gage when they conform to the approved closure and mechanical attachment requirements of Section M1601.3:

1.	Continuous welds.

2.	Snaplock seams and grooved, standing, double-corner, single-corner and Pittsburgh-lock seams and all other rolled mechanical seams.

3.	Mastic, mastic-plus-embedded fabric, or mastic ribbons.

4.	Gaskets.

5.	Pressure-sensitive tape.

6.	Aerosol sealant.

M1601.5.2 Pressure 1-inch water gage or greater, approved closure systems. The following closure systems are approved for rigid metal duct designed to be operated at pressures 1-inch water gage or greater and flexible duct when they conform to the approved closure and mechanical attachment requirements of Section M1601.3:

1.Continuous welds.

2.Mastic, mastic-plus-embedded fabric or mastic ribbons.

3.Gaskets.

M1601.5.3 High pressure duct systems. High pressure duct systems designed to operate at pressures greater than 3 inches water gauge (4 inches water gauge pressure class), shall be tested in accordance with the SMACNA HVAC Air Duct Leakage Test Manual. The tested duct leakage class, at a test pressure equal to the design duct pressure class rating, shall be equal to or less than Leakage Class 6. Leakage testing may be limited to representative sections of the duct system but in no case shall such tested sections include less than 25 percent of the total installed duct area for the designated pressure class.

M1601.6 Independent garage HVAC systems.  [Move to M1601.1.3.] Change 1601.6 to read as shown.

M1601.6 Nonmetallic ducts. Nonmetallic ducts shall be constructed with Class 0 or Class 1 duct material in accordance with UL 181. Fibrous duct construction shall conform to the SMACNA Fibrous Glass Duct Construction Standards or NAIMA Fibrous Glass Duct Construction Standards. The maximum air temperature with nonmetallic ducts shall not exceed 250°F (121°C).

M1601.6.1 Gypsum. Gypsum boards that form air shafts (ducts) shall be limited to return air systems where the air temperatures do not exceed 125°F (52°C) and the gypsum board surface temperature is maintained above the airstream dew-point temperature. Gypsum return air ducts shall not be incorporated in air-handling systems utilizing evaporative coolers.

M1601.6.2 Fibrous glass duct, rigid. All joints, seams and duct wall penetrations including, but not limited to, the joints between sections of duct and the joints between duct and other distribution system components shall be mechanically attached and sealed using approved closure systems as specified in Section M1601.3.

M1601.6.2.1 Approved closure systems. The following closure systems are approved for rigid fibrous glass ducts when they conform to the approved closure and mechanical attachment requirements of Section M1601.3:

1.	 Heat-activated tapes.

2.	 Pressure-sensitive tapes.

3.	Mastics or mastic-plus-embedded fabric systems.

M1601.6.2.2 Mechanical fastening. Attachments of ductwork to air handling equipment shall be by mechanical fasteners. Where access is limited, two fasteners on one side shall be acceptable when installed in accordance with Section M1601.3.6.

M1601.6.3 Flexible air duct systems, nonmetal. Flexible nonmetal ducts shall be joined to all other air distribution system components by either terminal or intermediate fittings. All duct collar fittings shall have a minimum 5/8 inch (16 mm) integral flange for sealing to other components and a minimum 3-inch (76 mm) shaft for insertion into the inner duct core.

Flexible ducts having porous inner cores shall not be used.

Exception: Ducts having a nonporous liner between the porous inner core and the outer jacket. Fastening and sealing requirements shall be applied to such intermediate liners.

All joints of flexible ducts to fittings and fittings to other air distribution system components shall be mechanically attached and sealed as specified in Sections M1601.6.3.1 through M1601.6.3.6.  Mechanical fasteners for use with flexible nonmetallic air ducts shall comply with UL 181B and shall be marked 181B-C. [M1601.4.1 IRC]

M1601.6.3.1 Duct core to duct fitting, mechanical attachment. The reinforced core shall be mechanically attached to the duct fitting by a drawband installed directly over the wire-reinforced core and the duct fitting. The duct fitting shall extend a minimum of 2 inches (51 mm) into each section of duct core. When the flexible duct is larger than 12 inches (305 mm) in diameter or the design pressure exceeds 1 inch water gauge, the drawband shall be secured by a raised bead or indented groove on the fitting.

M1601.6.3.2 Duct core to duct fitting, approved closure systems. The reinforced lining shall be sealed to the duct fitting using one of the following sealing materials which conforms to the approved closure and mechanical attachment requirements of Section M1601.3:

1.	Gasketing.

2.	Mastic, mastic-plus-embedded fabric or mastic ribbons.

3.	Pressure-sensitive tape.

4.	 Aerosol sealants, provided that their use is consistent with UL 181.

M1601.6.3.3 Duct outer jacket to duct collar fitting. The outer jacket of a flexible duct section shall be secured at the juncture of the air distribution system component and intermediate or terminal fitting in such a way as to prevent excess condensation. The outer jacket of a flexible duct section shall not be interposed between the flange of the duct fitting and the flexible duct, rigid fibrous glass duct board, or sheet metal to which it is mated.

M1601.6.3.4 Duct collar fitting to rigid duct, mechanical attachment. The duct collar fitting shall be mechanically attached to the rigid duct board or sheet metal by appropriate mechanical fasteners, either screws, spin-in flanges, or dovetail flanges.

M1601.6.3.5 Duct collar fitting to rigid duct, approved closure systems. The duct collar fitting’s integral flange shall be sealed to the rigid duct board or sheet metal using one of the following closure systems/materials which conforms to the approved closure and mechanical attachment standards of Section M1601.3:

1.Gasketing.

2.Mastic or mastic-plus-embedded fabric.

3.Mastic ribbons when used to attach a duct collar to sheet metal.

4.Pressure-sensitive tape.

5.Aerosol sealants, provided that their use is consistent with UL 181.

M1601.6.3.6 Flexible duct installation and support. Flexible ducts shall be configured and supported so as to prevent the use of excess duct material, prevent duct dislocation or damage, and prevent constriction of the duct below the rated duct diameter in accordance with the following requirements:

1.	Ducts shall be installed fully extended. The total extended length of duct material shall not exceed 5 percent of the minimum required length for that run.

2.	Bends shall maintain a center line radius of not less than one duct diameter.

3.	Terminal devices shall be supported independently of the flexible duct.

4.	 Horizontal duct shall be supported at intervals not greater than 5 feet (1524 mm). Duct sag between supports shall not exceed 1/2 inch (12.7 mm) per foot of length. Supports shall be provided within 1½ feet (457 mm) of intermediate fittings and between intermediate fittings and bends. Ceiling joists and rigid duct or equipment may be considered to be supports.

5.	Vertical duct shall be stabilized with support straps at intervals not greater than 6 feet (1829 mm).

6.	Hangers, saddles and other supports shall meet the duct manufacturer’s recommendations and shall be of sufficient width to prevent restriction of the internal duct diameter. In no case shall the material supporting flexible duct that is in direct contact with it be less than 1½ inches (38 mm) wide.

M1601.6.4 4.2 Plastic duct joints. Joints between plastic ducts and plastic fittings shall be made in accordance with the manufacturer’s installation instructions.

M1601.7 Terminal and intermediate fittings. All seams and joints in terminal and intermediate fittings, between fitting subsections and between fittings and other air distribution system components or building components shall be mechanically attached and sealed as specified in Section M1601.7.1 or Section M1601.7.2.

M1601.7.1 Fittings and joints between dissimilar duct types, approved closure systems. Approved closure systems shall be as designated by air distribution system component material type in Section M1601.3.

Exception: When the components of a joint are fibrous glass duct board and metal duct, including collar fittings and metal equipment housings, the closure systems approved for fibrous glass duct shall be used.

M1601.7.2 Terminal fittings and air ducts to building envelope components, approved closure systems. Terminal fittings and air ducts which penetrate the building envelope shall be mechanically attached to the structure and sealed to the envelope component penetrated and shall use one of the following closure systems/materials which conform to the approved closure and mechanical application requirements of Section M1601.3:

1.   Mastics or mastic-plus-embedded fabrics.

2.  Gaskets used in terminal fitting/grille assemblies which compress the gasket material between the fitting and the wall, ceiling or floor sheathing.

M1601.8 Air-handling units. All air-handling units shall be mechanically attached to other air distribution system components. Air-handling units located outside the conditioned space shall be sealed using approved closure systems conforming to the approved closure and M1601.5.1 and the mechanical application requirements of Section M1601.3. See Section M1305.1.3.

M1601.8.1 Approved closure systems. Systems conforming to the product and application standards of Section M1601.3 may be used when sealing air-handling units.

M1601.9 Cavities of the building structure.  Cavities in framed spaces, such as dropped soffits and walls, shall not be used to deliver air from or return air to the conditioning system unless they contain an air duct insert which is insulated in accordance with Table N1110.AB.2.1 and constructed and sealed in accordance with the requirements of Section M1601.3 appropriate for the duct materials used.

Exception: Return air plenums.

Cavities designed for air transport such as mechanical closets, chases, air shafts, etc., shall be lined with an air barrier and sealed in accordance with Section M1601.10 and shall be insulated in accordance with Table N1110.AB.2.1

Building cavities which will be used as return air plenums shall be lined with a continuous air barrier made of durable nonporous materials. All penetrations to the air barrier shall be sealed with a suitable long-life mastic material.

Exception: Surfaces between the plenum and conditioned spaces from which the return/mixed air is drawn.

Building cavities beneath a roof deck that will be used as return air plenums shall have an insulated roof with the insulation having an R-value of at least R-19.

M1601.10 Mechanical closets. The interior surfaces of mechanical closets shall be sheathed with a continuous air barrier as specified in Section M1601.10.1 and shall be sealed with approved closure systems as specified in Section M1601.10.2. All joints shall be sealed between air barrier segments and between the air barriers of walls and those of the ceiling, floor and door framing. All penetrations of the air barrier including, but not limited to, those by air ducts, plenums, pipes, service lines, refrigerant lines, electrical wiring, and condensate drain lines shall be sealed to the air barrier and approved closure systems.

Exception: Air passageways into the closet from conditioned space that are specifically designed for return air flow.

Through-wall, through-floor and through-ceiling air passageways into the closet shall be framed and sealed to form an airtight passageway using approved air duct materials and approved closure systems.

Duct penetrations through any part of the ceiling, walls or floor of a mechanical closet shall have sufficient space between surrounding ceiling, walls or floor and any duct or plenum penetration to allow for sealing of the penetration and inspection of the seal.

Clothes washers, clothes dryers, combustion water heaters and atmospheric combustion furnaces shall not be located in mechanical closets used as return air plenums.

M1601.10.1 Approved air barriers. The following air barriers are approved for use in mechanical closets:

1.	One-half inch (12.7 mm) thick or greater gypsum wallboard, taped and sealed.

2.	Other panelized materials having inward facing surfaces with an air porosity no greater than that of a duct product meeting Section 22 of UL 181 which are sealed on all interior surfaces to create a continuous air barrier.

M1601.10.2 Approved closure systems. The following closure systems are approved for use in mechanical closets:

1. Gypsum wallboard joint compound over taped joints between gypsum wallboard panels.

2. Sealants complying with the product and application standards of Sec. M1601.6.3.1 for fibrous glass ductboard;

3. A suitable long-life caulk or mastic compliant with the locally adopted mechanical code for all applications.

M1601.11 Enclosed support platforms. Enclosed support platforms located between the return air inlet(s) from conditioned space and the inlet of the air handling unit or furnace, shall contain a duct section constructed entirely of rigid metal, rigid fibrous glass duct board, or flexible duct which is constructed and sealed according to the respective requirements of Section M1601.3 and insulated according to the requirements of Section N1110

The duct section shall be designed and constructed so that no portion of the building structure, including adjoining walls, floors and ceilings, shall be in contact with the return air stream or function as a component of this duct section.

The duct section shall not be penetrated by a refrigerant line chase, refrigerant line, wiring, pipe or any object other than a component of the air distribution system.

Through-wall, through-floor and through-ceiling penetrations into the duct section shall contain a branch duct which is fabricated of rigid fibrous glass duct board or rigid metal and which extends to and is sealed to both the duct section and the grille side wall surface. The branch duct shall be fabricated and attached to the duct insert in accordance with Section M1601.5 or Section M1601.6.2, respective to the duct type used.

TABLE M1601.4

DUCT SYSTEM CONSTRUCTION AND SEALING

| DUCT TYPE/CONNECTION | SEALING REQUIREMENTS | MECHANICAL ATTACHMENT | TEST STANDARD |
| --- | --- | --- | --- |
| Metal duct, rigid and flexible |  |  |  |
| Pressures less than 1-inch water gauge | Closure systems as described in Section M1601.4.1.7: 1. Continuous welds. 2. Snaplock seams, and grooved, standing, double-corner, single-corner and Pittsburgh-lock seams and all other rolled mechanical seams. 3. Mastic, mastic-plus-embedded fabric, or mastic ribbons. ` 4. Gaskets. 5. Pressure-sensitive tape. | Mechanical attachments approved: 1. Continuous welds. 2. Snaplock seams, and grooved, standing, double-corner, single-corner and Pittsburgh-lock seams and all other rolled mechanical seams. Crimp joints for round metal ducts shall have a contact lap of at least 11/2inches (38 mm) and shall be mechanically fastened by means of at least three sheet-metal screws or rivets equally spaced around the joint. | SMACNA HVAC Air Duct Leakage Test Manual |
| Pressures 1-inch water gauge or greater | Closure systems as described in Section M1601.4.1.7: 1. Continuous welds. 2. Mastic or mastic-plus-embedded fabric systems. 3. Gaskets. | Mechanical attachments approved: 1. Continuous welds | SMACNA HVAC Air Duct Leakage Test Manual |
| High pressure duct systems designed to operate at pressures greater than 3-inch water gauge (4-inch water gauge pressure class) | Shall be tested in accordance with the standard . The tested duct leakage class, at a test pressure equal to the design duct pressure class rating, shall be equal to or less than Leakage Class 6. Leakage testing may be limited to representative sections of the duct system but in no case shall such tested sections include less than 25 percent of the total installed duct area for the designated pressure class. |  | SMACNA HVAC Air Duct Leakage Test Manual |
| Plastic duct |  | Joints between plastic ducts and plastic fittings shall be made in accordance with the manufacturer’s installation instructions. |  |
| Fibrous glass duct, rigid. | All joints, seams and duct wall penetrations between sections of duct and between duct and other distribution system components shall be sealed with closure systems as described in Section M1601.4.1.7: 1. Heat-activated tapes. 2. Pressure-sensitive tapes. 3. Mastics or mastic-plus-embedded fabric systems. | Mechanically fastened per standard to secure the sections independent of the closure system(s). Attachments of ductwork to air-handling equipment shall be by mechanical fasteners in accordance with Section M1601.4.1.1. Where access is limited, two fasteners on one side shall be acceptable. | NAIMA Fibrous Glass Duct Construction Standards. UL 181 UL 181A |
| Flexible duct systems, nonmetal. | All duct collar fittings shall have a minimum 5/8 inch (16 mm) integral flange for sealing to other components and a minimum 3-inch (76 mm) shaft for insertion into the inner duct core. Flexible ducts having porous inner cores shall not be used. Exception: Ducts having a nonporous liner between the porous inner core and the outer jacket. Fastening and sealing requirements shall be applied to such intermediate liners. | Flexible nonmetal ducts shall be joined to all other air distribution system components by either terminal or intermediate fittings. Mechanical fasteners for use with flexible nonmetallic air ducts shall comply with UL 181B and shall be marked 181B-C. | UL 181 UL 181B |
| Duct core to duct fitting | The reinforced lining shall be sealed to the duct fitting using one of the following sealing materials which conforms to the approved closure and mechanical attachment requirements of Section M1601.4.1.7: 1. Gasketing. 2. Mastic, mastic-plus-embedded fabric, or mastic ribbons. 3. Pressure-sensitive tape. 4. Aerosol sealants, provided that their use is consistent with UL 181. | The reinforced core shall be mechanically attached to the duct fitting by a drawband installed directly over the wire-reinforced core and the duct fitting. The duct fitting shall extend a minimum of 2 inches (51 mm) into each section of duct core. When the flexible duct is larger than 12 inches (303 mm) in diameter or the design pressure exceeds 1-inch water gauge, the drawband shall be secured by a raised bead or indented groove on the fitting. |  |
| Duct outer jacket to duct collar fitting | The outer jacket of a flexible duct section shall be secured at the juncture of the air distribution system component and intermediate or terminal fitting in such a way as to prevent excess condensation. The outer jacket of a flexible duct section shall not be interposed between the flange of the duct fitting and the flexible duct, rigid fibrous glass duct board, or sheet metal to which it is mated. |  |  |
| Duct collar fitting to rigid duct | The duct collar fitting’s integral flange shall be sealed to the rigid duct board or sheet metal using one of the following closure systems/materials which conforms to the approved closure and mechanical attachment standards of Section M1601.4.1.7: 1. Gasketing. 2. Mastic or mastic-plus-embedded fabric systems. 3. Mastic ribbons when used to attach a duct collar to sheet metal. 4. Pressure-sensitive tape. 5. Aerosol sealants, provided that their use is consistent with UL 181. | The duct collar fitting shall be mechanically attached to the rigid duct board or sheet metal by appropriate mechanical fasteners, either screws, spin-in flanges, or dovetail flanges. |  |
| Terminal and intermediate fittings. Fittings and joints between dissimilar duct types Terminal fittings and air ducts to building envelope components | Approved closure systems shall be as designated by air distribution system component material type in Section M1601.4.1.7. Exception: When the components of a joint are fibrous glass duct board and metal duct, including collar fittings and metal equipment housings, the closure systems approved for fibrous glass duct shall be used. Terminal fittings and air ducts which penetrate the building envelope shall be mechanically attached to the structure and sealed to the envelope component penetrated and shall use one of the following closure systems/materials which conform to the approved closure and mechanical application requirements of Section M1601.4.1.7: 1. Mastics or mastic-plus-embedded fabrics. 2. Gaskets used in terminal fitting/grille assemblies which compress the gasket material between the fitting and the wall, ceiling or floor sheathing. |  |  |
| Air-handling units. | Air-handling units located outside the conditioned space shall be sealed using approved closure systems described in Section M1601.4.1.7 | All air-handling units shall be mechanically attached to other air distribution system components. |  |
| Return plenums. | Building cavities which will be used as return air plenums shall be lined with a continuous air barrier made of durable nonporous materials. All penetrations to the air barrier shall be sealed with a suitable long-life mastic material. Exception: Surfaces between the plenum and conditioned spaces from which the return/mixed air is drawn. |  |  |
| Mechanical closets. | All joints between the air barriers of walls, ceiling, floor and door framing and all penetrations of the air barrier shall be sealed to the air barrier with approved closure systems. Through-wall, through-floor and through-ceiling air passageways into the closet shall be framed and sealed to form an air-tight passageway. Exception: Air passageways into the closet from conditioned space that are specifically designed for return air flow. The following air barriers are approved for use in mechanical closets: 1. One-half-inch-thick (12.7 mm) or greater gypsum wallboard, taped and sealed. 2. Other panelized materials having inward facing surfaces with an air porosity no greater than that of a duct product meeting Section 22 of UL 181 which are sealed on all interior surfaces to create a continuous air barrier. | The following closure systems are approved for use in mechanical closets: 1. Gypsum wallboard joint compound over taped joints between gypsum wallboard panels. 2. Sealants complying with the product and application standards of ths table for fibrous glass ductboard. 3. A suitable long-life caulk or mastic compliant with the locally adopted mechanical code for all applications. |  |
| Enclosed support platforms in unconditioned spaces. | Enclosed support platforms located between the return air inlet(s) from conditioned space and the inlet of the air-handling unit or furnace, shall contain a duct section constructed entirely of rigid metal, rigid fibrous glass duct board, or flexible duct which is constructed and sealed according to the respective requirements of Section M1601.4.1.7 and insulated according to the requirements of Section 403.2.1 of the Florida Building Code, Energy Conservation. No portion of the building structure, including adjoining walls, floors and ceilings, shall be in contact with the return air stream or function as a component of this duct section |  |  |

Overlap with Florida Specific – Mechanical TAC

Parts of Section M1601.5 have been changed. Renumber to M1601.12. Consider possible conflicts.

If Florida Sections M1601.5 through M1601.11 are tablified and referenced from Section M1601.4, no renumbering is required for Under-floor plenum text.

M1601.12 5 Under-floor plenums. Under-floor plenums shall be prohibited in new structures. Modification or repairs to under-floor plenums in existing structures shall conform to the requirements of this section.

M1601.12 5.1 General. The space shall be cleaned of loose combustible materials and scrap, and shall be tightly enclosed. The ground surface of the space shall be covered with a moisture barrier having a minimum thickness of 4 mils (0.1 mm). Plumbing waste cleanouts shall not be located within the space.

Exception: Plumbing waste cleanouts shall be permitted to be located in unvented crawl spaces that receive conditioned air in accordance with Section R408.3.

M1601.12 5.2 Materials. The under-floor space, including the sidewall insulation, shall be formed by materials having flame-spread ratings not greater than 200 when tested in accordance with ASTM E 84.

M1601.12 5.3 Furnace connections. A duct shall extend from the furnace supply outlet to not less than 6 inches (152 mm) below the combustible framing. This duct shall comply with the provisions of Section M1601.1. A noncombustible receptacle shall be installed below any floor opening into the plenum in accordance with the following requirements:

1. The receptacle shall be securely suspended from the floor members and shall not be more than 18 inches (457 mm) below the floor opening.

2. The area of the receptacle shall extend 3 inches (76 mm) beyond the opening on all sides.

3. The perimeter of the receptacle shall have a vertical lip at least 1 inch (25 mm) high at the open sides.

M1601.13 6 Independent garage HVAC systems. Furnaces and air-handling systems that supply air to living spaces shall not supply air to or return air from a garage. [OR Leave as is in IRC M1601.6.]

Staff recommendation:  Using the Table referenced above is a code change.  Consider using the IRC09 provisions as noted above.

M1602  RETURN AIR

M1602.1 – M1602.3  [No change]

M1602.4 Balanced return air.    Add to read as shown.

M1602.4 Balanced return air.  Restricted return air occurs in buildings when returns are located in central zones and closed interior doors impede air flow to the return grill or when ceiling spaces are used as return plenums and fire walls restrict air movement from one portion of the return plenum to another. Provisions shall be made in residential buildings to avoid unbalanced air flows and pressure differentials caused by restricted return air. Pressure differentials across closed doors where returns are centrally located shall be limited to 0.01 inch WC (2.5 pascals) or less. Pressure differentials across fire walls in ceiling space plenums shall be limited to 0.01 inch WC (2.5 pascals) by providing air duct pathways or air transfer pathways from the high pressure zone to the low zone.

Exceptions:

1.	Transfer ducts may achieve this by increasing the return transfer one and one half times the cross sectional area (square inches) of the supply duct entering the room or space it’s serving and the door having at least an unrestricted 1 inch (25 mm) undercut to achieve proper return air balance.

2.	Transfer grilles shall use 50 square inches (4.6 mm) (of grille area) to 100 cfm (0.05 m3/s) (of supply air) for sizing through-the-wall transfer grilles and using an unrestricted 1-inch (25 mm) undercutting of doors to achieve proper return air balance

3.	Habitable rooms only shall be required to meet these requirements for proper balanced return air excluding bathrooms, closets, storage rooms and laundry rooms, except that all supply air into the master suite shall be included.

Chapter 17, Combustion Air (No change)

Chapter 18, Chimneys and Vents. [No change.]

Chapter 19, Special Fuel-Burning Equipment. [No change.]

Chapter 20, Boilers and Water Heaters

Section M2005 Water Heaters

M2005.3 Electric water heaters.  Change to read as shown.

M2005.3 Electric water heaters. Electric water heaters shall also be installed in accordance with the applicable provisions of Chapter 34.

Section M2006 Pool Heaters

M2006.1 General.  Change to read as shown.

M2006.1 General. Pool and spa heaters shall be installed in accordance with the manufacturer’s installation instructions. Oil-fired pool heaters shall be tested in accordance with UL 726. Electric pool and spa heaters shall be tested in accordance UL 1261. See Section 13-612.AB.2.3.2 of the Florida Building Code, Building.

Chapter 21, Hydronic Piping

Section M2101 Hydronic Piping Systems Installation

M2101.6 Drilling and notching.    Change to read as shown.

M2101.6 Drilling and notching. Wood-framed structural members shall be drilled, notched or altered in accordance with the provisions of Sections R502.2.8, R602.2.6, R602 .2.7.1 and R802.2.4. Holes in load bearing members of cold-formed steel light-frame construction shall be permitted only in accordance with Sections R505.2.5, R603.2.5 and R804.2.5. In accordance with the provisions of Sections R505.3.5, R603.3.4 and R804.3.4, cutting and notching of flanges and lips of load-bearing members of cold-formed steel light-frame construction shall not be permitted. Structural insulated panels (SIPs) shall be drilled and notched or altered in accordance with the provisions of Section R614.

Chapter 22, Special Piping and Storage Systems

Section M2203 Installation

M2203.5 Vent termination.    Change to read as shown.

M2203.5 Vent termination. Vent piping shall terminate outside of buildings at a point not less than 2 feet (610 mm), measured vertically or horizontally, from any building opening. Outer ends of vent piping shall terminate in a weather-proof cap or fitting having an unobstructed area at least equal to the cross-sectional area of the vent pipe, and shall be located sufficiently above the ground to avoid being obstructed.

Chapter 23, Solar Systems [No change.]

Part VI – Fuel Gas

Chapter 24, Fuel Gas

Change to read as shown.

The text of this chapter is excerpted from the 2009 edition of the Florida Building Code, Fuel Gas and has been modified where necessary to make such text conform to the scope of application of the Florida Building Code, Residential. The section numbers appearing in parentheses after each section number represent the location of the corresponding text in the Florida Building Code, Fuel Gas.

Section G2403 General Definitions

G2403 Definitions.  Change to read as shown.

REGULATOR. A device for controlling and maintaining a uniform gas supply pressure, either pounds to pounds, pounds-to-inches water column (MP regulator) or inches-to-inches water column (appliance regulator).

RISER, GAS. A vertical pipe supplying fuel gas to a meter assembly or pressure regulator.

Section G2404 (301) General

G2404.2 (301.1.1) Other fuels. Change to read as shown.

G2404.2 (301.1.1)   This code shall apply to the installation of fuel gas piping systems, fuel gas utilization equipment, and related accessories as follows:

1.	Coverage of piping systems shall extend from the point of delivery to the connections with gas utilization equipment (see “Point of delivery”).

2.	Systems with an operating pressure of 125 psig (862 kPa gauge) or less.

Piping systems for gas-air mixtures within the flammable range with an operating pressure of 10 psig (69 kPa gauge).

LP-gas piping systems with an operating pressure of 20 psig (140 kPa) or less.

3.	Piping systems requirements shall include design, materials, components, fabrication, assembly, installation, testing, inspection, operation and maintenance.

4.	Requirements for gas utilization equipment and related accessories shall include installation, combustion and ventilation air and venting.

This code shall not apply to the following:

1.	Portable LP-gas equipment of all types that are not connected to a fixed fuel piping system.

2.	Installation of farm equipment such as brooders, dehydrators, dryers and irrigation equipment.

3.	Raw material (feedstock) applications except for piping to special atmosphere generators.

4.	Oxygen-fuel gas cutting and welding systems.

5.	Industrial gas applications using gases such as acetylene and acetylenic compounds, hydrogen, ammonia, carbon monoxide, oxygen and nitrogen.

6.	Petroleum refineries, pipeline compressor or pumping stations, loading terminals, compounding plants, refinery tank farms and natural gas processing plants.

7.	Integrated chemical plants or portions of such plants where flammable or combustible liquids or gases are produced by chemical reactions or used in chemical reactions.

8.	LP-gas installations at utility gas plants.

9.	Liquefied natural gas (LNG) installations.

10.	Fuel gas piping in power and atomic energy plants.

11.	Proprietary items of equipment, apparatus, or instruments such as gas generating sets, compressors and calorimeters.

12.	LP-gas equipment for vaporization, gas mixing and gas manufacturing.

13.	Temporary LP-gas piping for buildings under construction or renovation that is not to become part of the permanent piping system.

14.	Installation of LP-gas systems for railroad switch heating.

15.	Installation of LP-gas and compressed natural gas (CNG) systems on vehicles.

16.	Gas piping, meters, gas pressure regulators, and other appurtenances used by the serving gas supplier in the distribution of gas, other than undiluted LP-gas.

17.	Building design and construction, except as specified herein.

G2404.8 (301.12) Seismic resistance.  Change to read as shown.

G2404.8 (301.12) Seismic resistance. Reserved.

G2404.11 (301.7)  Fuel types.  Add to read as shown.

G2404.11 (301.7)  Fuel types. Fuel-fired appliances shall be designed for use with the type of fuel gas to which they will be connected and the altitude at which they are installed.  Appliances that comprise parts of the installation shall not be converted for the usage of a different fuel, except where approved and converted in accordance with the manufacturer’s instructions or the serving gas supplier.  The fuel gas input rate shall not be increased or decreased beyond the limit rating for the altitude at which the appliance is installed.

Overlap with Florida Specific – Plumbing TAC

Section G2408 (305) Installation

FBC

G2408.2 (305.3) Water heaters installed in garages.  Change to read as shown. Need to be resolved.

G2408.2 (305.3) Water heaters installed in garages. Water heaters shall be installed in accordance with the manufacturer’s instructions which shall be available on the job site at the time of inspection.

The IRC ’09 has been changed to add the following section. Resolve potential conflicts.

G2408.2 (305.3) Elevation of ignition source. Equipment and appliances having an ignition source shall be elevated such that the source of ignition is not less than 18 inches (457 mm) above the floor in hazardous locations and public garages, private garages, repair garages, motor fuel-dispensing facilities and parking garages. For the purpose of this section, rooms or

spaces that are not part of the living space of a dwelling unit and that communicate directly with a private garage through openings shall be considered to be part of the private garage.

Exception: Elevation of the ignition source is not required for appliances that are listed as flammable vapor ignition resistant.

2009 IRC

G2408.2.1 (305.3.1) Installation in residential garages. In residential garages where appliances are installed in a separate, enclosed space having access only from outside of the garage, such appliances shall be permitted to be installed at floor level, provided that the required combustion air is taken from the exterior of the garage.

Staff recommendation:  Florida specific provisions are not covered by the IRC09.  Consider continue using Florida specific provisions.

Section G2410 Electrical

G2410.1 (309.1) Grounding.  Change to read as shown.

G2410.1 (309.1) Grounding. Each above-ground portion of a gas piping system upstream from the equipment shutoff valve shall be electrically continuous and bonded to any grounding electrode as defined by the Chapter 34of this code.

Section G2412 General

G2412.2 (401.2) Liquefied petroleum gas storage.  Change to read as shown.

G2412.2 (401.2) Liquefied petroleum gas storage. The storage system (container, regulators, piping and all components upstream to the point of delivery) for liquefied petroleum gas shall be designed and installed in accordance with the Florida Fire Prevention Code and NFPA 58.

Overlap with Florida Specific – Plumbing TAC

G2412.5 (401.5) Identification.  Change to read as shown.  Need to be resolved.

FBC

G2412.5 (401.5) Identification. For other than black steel pipe, exposed piping shall be identified by a yellow label marked “Gas” in black letters. The marking shall be spaced at intervals not exceeding 5 feet (1524 mm). The marking shall not be required on pipe located in the same room as the equipment served.

Exception: This section shall only apply where other similar piping or tubing in the same general area as the gas lines, containing a different medium, could be confused with the gas lines.

[Exception was in the ’01 FBC-FG, not ’04 or ’07. Correlate with FBC-FG; the only difference is that the word “appliance” has replaced “equipment”. Recommend use IFGC]

IRC-FG ’09 has been changed as shown. Resolve potential conflicts.

G2412.5 (401.5) Identification. For other than steel pipe, exposed piping shall be identified by a yellow label marked “Gas” in black letters. The marking shall be spaced at intervals not exceeding 5 feet (1524 mm). The marking shall not be required on pipe located in the same room as the appliance served.

Staff recommendation: Florida specific provisions are not covered by the IRC09.  Consider continue using Florida specific provisions.

Section G2415 Piping System Installation

G2415.15.3 (404.15.3) Tracer. Change to read as shown.

G2415.15.3 (404.15.3) Tracer.  An insulated copper tracer wire or other approved conductor shall be installed adjacent to underground nonmetallic gas piping. Access shall be provided to the tracer wire or the tracer wire shall terminate above ground at each end of the nonmetallic gas piping. The tracer wire size shall not be less than 18 AWG and the insulation type shall be suitable for direct burial.

Section G2417 (406) Inspection, Testing and Purging

G2417.3.4 (406.3.4) Valve isolation.  Change to read as shown.

G2417.3.4 (406.3.4) Valve isolation.  Where the piping system is connected to equipment or components designed for operating pressures of less than the test pressure, such equipment or components shall be isolated from the piping system by disconnecting them and plugging or capping the outlet(s).

G2417.7.4 (406.7.4) Placing equipment in operation.  Change to read as shown.

G2417.7.4 (406.7.4) Placing equipment in operation. After the piping has been placed in operation, all equipment shall be placed in operation per its listing and the manufacturer’s instructions.

Section G2422 (411) Appliance Connections

G2422.1.6 (411.1.7) Outdoor appliance connectors.  Add to read as shown.

G2422.1.6 (411.1.7) Outdoor appliance connectors. Outdoor gas hose connectors are permitted to connect portable outdoor gas-fired equipment.  An equipment shutoff valve, a listed quick-disconnect device, or a listed gas convenience outlet shall be installed where the connector is attached to the supply piping and in such a manner as to prevent the accumulation of foreign matter.  Lengths shall not exceed 12 feet (3658 mm) and the connection shall only be made in the outdoor area where the equipment is to be used.

Part VII - Plumbing

Chapter 25, Plumbing Administration

Section P2502 Existing Plumbing Systems

P2502.1 Existing building sewers and drains.  Change to read as shown.

P2502.1 Existing building sewers and drains. See Florida Building Code, Existing Building.

Section P2503 Inspection and Tests

P2503.4 Gravity sewer test.  Change to read as shown.

P2503.4 Gravity sewer test. Gravity sewer tests shall consist of plugging the end of the building sewer at the point of connection with the public sewer, completely filling the building sewer with water from the lowest to the highest point thereof, and maintaining such pressure for 15 minutes. The building sewer shall be water tight at all points.

P2503.5.1 Drainage and vent water test.  Change to read as shown.

P2503.5.1 Drainage and vent water test. A water test shall be applied to the drainage system either in its entirety or in sections. If applied to the entire system, all openings in the piping shall be tightly closed, except the highest opening, and the system shall be filled with water to point of overflow. If the system is tested in sections, each opening shall be tightly plugged except the highest openings of the section under test, and each section shall be filled with water, but no section shall be tested with less than a 5-foot (1524 mm) head of water. In testing successive sections, at least the upper 5 feet (1524 mm) of the next preceding section shall be tested so that no joint or pipe in the building, except the uppermost 5 feet (1524 mm) of the system, shall have been submitted to a test of less than a 5-foot (1524 mm) head of water. The water shall be kept in the system, or in the portion under test, for at least 15 minutes before inspection starts. The system shall then be tight at all points.

P2503.8.2 Testing.  Change to read as shown.

P2503.87.2 Testing.  Reduced pressure principle backflow preventers, double check valve assemblies, double-detector check valve assemblies and pressure vacuum breaker assemblies shall be tested at the time of installation, immediately after repairs or relocation and at least annually.

Chapter 26, General Plumbing Requirements

Section P2603 Structural and Piping Protection

P2603.2 Drilling and notching.  Change to read as shown.

P2603.2 has been changed. Resolve potential conflicts.

P2603.2 Drilling and notching. Wood-framed structural members shall not be drilled, notched or altered in any manner except as provided in Sections R502.2.8, R602.1.3.15, R602.2.7, R802.2.6 and R802.2.6.1. Holes in load-bearing members of cold-formed steel light-frame construction shall be permitted only in accordance with Sections R505.3.5, R603.2.5 and R804.2.5. In accordance with the provisions in Sections R505.3.5, R603.3.4 and R804.3.4, cutting and notching of flanges and lips of  load-bearing members of cold-formed steel light-frame construction shall not be permitted. Structural insulated panels (SIPs) shall be drilled and notched or altered in accordance with the provisions of Section R613.7.

P2603.2.1 Protection against physical damage. In concealed locations, where piping, other than cast-iron or galvanized steel, is installed through holes or notches in studs, joists, rafters or similar members less than 11/2 inches (38 mm) from the nearest edge of the member, the pipe shall be protected by steel shield plates. Such shield plates shall have  a thickness of not less than 0.0575 inch (1.463 mm) (No. 16 Gage). Such plates shall cover the area of the pipe where the member is notched or bored, and shall extend a minimum of 2 inches (51 mm) above sole plates and below top plates.

Overlap with Florida Specific – Plumbing TAC

Section P2603.3 Breakage and corrosion. Revise text to read as follows: Need to be resolved.

FBC

P2603.3 Breakage and corrosion. Pipes passing through concrete or cinder walls and floors or other corrosive material shall be protected against external corrosion by a protective sheathing or wrapping or other means that will withstand any reaction from lime and acid of concrete, cinder or other corrosive material. Sheathing or wrapping shall allow for expansion and contraction of piping to prevent any rubbing action. Minimum wall thickness of material shall be 0.010 inch (0.28 0.64 mm).

Exception: Sleeving is not required for installation of CPVC into concrete or similar material

2009 IRC P2603.3 has been changed. Resolve potential conflicts:

P2603.3 Breakage and corrosion. Pipes passing through or under walls shall be protected from breakage. Pipes passing through concrete or cinder walls and floors, cold-formed steel framing or other corrosive material shall be protected against external corrosion by a protective sheathing or wrapping or other means that will withstand any reaction from lime and acid of concrete, cinder or other corrosive material. Sheathing or wrapping shall allow for movement including expansion and contraction of piping to prevent any rubbing action. Minimum wall thickness of material shall be 0.025 inch (0.64 mm).

Staff recommendation:  Florida specific provisions are not covered by the IRC09.  Consider using the IRC09 provisions as the base text and revise to add into it Florida specific provisions.

Section P2603.3.1 Penetration add text to read as follows:

P2603.3.1 Penetration. Protective sleeves around piping penetrating concrete slab-on-grade floors shall not be of cellulose-containing materials. If soil treatment is used for subterranean termite protection, the sleeve shall have a maximum wall thickness of 0.010 inch, and be sealed within the slab using a non-corrosive clamping device to eliminate the annular space between the pipe and the sleeve. No termiticides shall be applied inside the sleeve.

P2603.6 Freezing.  Change to read as shown.

P2603.6 Freezing. Where the design temperature is less than 32°F (0°C), a water, soil or waste pipe shall not be installed outside of a building, in attics or crawl spaces, or be concealed in outside walls in any location subjected to freezing temperatures, unless adequate provision is made to protect them from freezing by insulation or heat or both. A water service pipe shall be installed not less than 12 inches (305 mm) deep or less than 6 inches (152 mm) below the frost line.

Chapter 27, Plumbing Fixtures

Table P2701.1 Plumbing Fixtures, Faucets and Fixture Fittings, revise text to read as follows:

TABLE P2701.1

PLUMBING FIXTURES, FAUCETS AND FIXTURE FITTINGS

(Only relevant section of table shown below)

| Material | Standard |
| --- | --- |
| Suction fittings for use in swimming pools, wading pools, spas, hot tubs and whirlpool bathtub appliances | ASME A112.19.8M |

IRC TABLE P2701.1 has been changed, but not in the “Suction fittings” category. No apparent conflict.

Section P2709 Shower Receptors

Overlap with Florida Specific – Plumbing TAC

P2709.2 Lining required.  Change to read as shown.  Need to be resolved.

FBC

P2709.2 Lining required. The adjoining walls and floor framing, enclosing on-site built-up shower receptors shall be lined with sheet lead, copper or a plastic liner material that complies with ASTM D 4068 or ASTM D 4551. The lining material shall extend not less than 3 inches (76 mm) beyond or around the rough jambs and not less than 3 inches (76 mm) above finished thresholds. Hot mopping shall be permitted in accordance with Section P2709.2.3.

Exceptions:

1. Floor surfaces under showerheads provided for rinsing laid directly on the ground.

2. Shower compartments where the finished shower drain is depressed a minimum of 2 inches (51 mm) below the surrounding finished floor on the first floor level and the shower recess is poured integrally with the adjoining floor.

The 2009 IRC P2709.2 has been changed. Resolve potential conflicts.

P2709.2 Lining required. The adjoining walls and floor framing enclosing on-site built-up shower receptors shall be lined with one of the following materials:

1. Sheet lead,

2. Sheet copper,

3. Plastic liner material that complies with ASTM D 4068 or ASTM D 4551,

4. Hot mopping in accordance with Section P2709.2.3 or

5. Sheet-applied load-bearing, bonded waterproof membranes that comply with ANSI A118.10.

The lining material shall extend not less than 3 inches (76 mm) beyond or around the rough jambs and not less than 3 inches (76 mm) above finished thresholds. Sheet-applied load

bearing, bonded waterproof membranes shall be applied in accordance with the manufacturer’s installation instructions.  Hot mopping shall be permitted in accordance with Section P2709.2.3.

Staff recommendation:  Florida specific provisions are not covered by the IRC09.  Consider using the IRC09 provisions as the base text and revise to add into it Florida specific provisions.

Chapter 28, Water Heaters

Section P2801 General

Overlap with Florida Specific – Plumbing TAC

P2801.5 Required pan.  Change to read as shown. Need to be resolved.

FBC

P2801.5 Required pan. Where water heaters or hot water storage tanks are installed above the ground floor space, or in attics or ceiling areas, or within the habitable space, the tank or water heater shall be installed in a galvanized steel or other metal pan of equal corrosion resistance having a minimum thickness of 24 gage, 0.0276 inch (0.70 mm). Electric water heaters shall be installed in a metal pan as herein required or in a high-impact plastic pan of at least 0.0625 inch (1.59 mm) thickness.

[no change to the remaining text]

2009 IRC P2801.5 has been changed. Resolve potential conflicts.

P2801.5 Required pan. Where water heaters or hot water storage tanks are installed in locations where leakage of the tanks or connections will cause damage, the tank or water heater shall

be installed in a galvanized steel pan having a material minimum thickness of not less than 0.0236 inch (0.6010 mm) (No. 24 gage) (0.016 inch(0.4 mm), or other pans approved for such use. Listed pans shall comply with CSA LC3.

Staff recommendation:  Florida specific provisions are not covered by the IRC09.  Consider using the IRC09 provisions as the base text and revise to add into it Florida specific provisions.

P2801.6 Water heaters installed in garages.  Change to read as shown.

P2801.6 Water heaters installed in garages. Water heaters shall be installed in accordance with the manufacturer’s installation instructions which shall be available on the job site at the time of inspection.

Section P2803 Relief Valves

P2803.6.2 Add to read as shown:

P2803.6.2 Relief outlet waste. The outlet of a pressure, temperature or other relief valve shall not be directly connected to the drainage system.

P2803.6.2.1 Discharge. The relief valve shall discharge full size to a safe place of disposal such as the floor, water heater pan, outside the building or an indirect waste receptor. The discharge pipe shall not have any trapped sections and shall have a visible air gap or air gap fitting located in the same room as the water heater. The discharge shall be installed in a manner that does not cause personal injury to occupants in the immediate area or structural damage to the building.

Chapter 29, Water Supply and Distribution

Section P2903 Water-supply System

P2903.1 Water supply system design criteria.  Change to read as shown.

P2903.1 Water supply system design criteria. The water service and water distribution systems shall be designed and pipe sizes shall be selected such that under conditions of peak demand, the capacities at the point of outlet discharge shall not be less than shown in Table P2903.1. Table P2903.2b shall be permitted to be used to size the water service or water distribution system.

Table P2903.2b Minimum Water Service Size.  Add to read as shown.

TABLE P2903.2b MINIMUM WATER SERVICE SIZEa

| NO. OF FIXTURE UNITS FLUSH TANK WCb | DIAMETER OF WATER PIPEc | RECOMMENDED METER SIZE (inches)d | APPROX. PRESSURE LOSS METER + 100’ PIPE (psi)e | NO. OF FIXTURE UNITS FLUSH VALVE WCb |
| --- | --- | --- | --- | --- |
| 18 | ¾ | 5/8 | 30 | — |
| 19-55 — | 1 1 | 1 1 | 30 30 | — 9 |
| 56-85 — | 1¼ 1¼ | 1 1 | 30 30 | — 10-20 |
| 86-225 — | 1½ 1½ | 1½ 1½ | 30 30 | — 21-77 |
| 226-350 — | 2 2 | 1½ 1½ | 30 30 | — 78-175 |
| 351-550 — | 2 2 | 2 2 | 30 30 | — 176-315 |
| 551-640 — | 2½ 2½ | 2 2 | 30 30 | — 316-392 |
| 641-1340 — | 3 3 | 3 3 | 22 22 | — 393-940 |

a. Table is applicable for both copper and plastic water piping.

b. See Table P3004.1 for fixture unit values.

c. Minimum water service shall be ¾” to control valve.

d. All secondary submeters and backflow assemblies shall be at least the same size as the line in which they are installed.

e. Table based on minimum water main pressure of 50 psi.

Chapter 30, Sanitary Drainage

P3001.2 Protection from freezing.  Change to read as shown.

P3001.2 Protection from freezing. Where the design temperature is less than 32°F (0°C), a water, soil or waste pipe shall not be installed outside of a building, in attics or crawl spaces, or be concealed in outside walls in any location subjected to freezing temperatures, unless adequate provision is made to protect them from freezing by insulation or heat or both. Water service pipe shall be installed not less than 12 inches (305 mm) deep or less than 6 inches (152 mm) below the frost line.

Section P3003 Joints and Connections

P3003.19  Floor and wall drainage connections.  Change to read as shown.

P3003.19  Floor and wall drainage connections. Connections between the drain and the floor outlet plumbing fixtures shall be made with a floor flange.  The flange shall be attached to the drain and anchored to the structure. Connections between the drain and wall-hung water closets shall be made with an approved extension nipple or horn adaptor. The water closet shall be bolted to the hanger with corrosion resistant bolts or screws. Joints shall be sealed with an approved elastometric gasket or setting compound conforming to FS TT-P-1536a.

P3003.19.1 Floor flanges.  Add to read as shown.

P3003.19.1 Floor flanges. Floor flanges for water closets or similar fixtures shall not be less than 1/8 inch (3.2 mm) thick for brass, ¼ inch (6.4 mm) thick for plastic and ¼ thick (6.4 mm) thick and not less than a 2-inch (51 mm) calking depth for cast-iron or galvanized malleable iron. Floor flanges of hard lead shall weigh not less than 1 pound 9 ounces (0.7 kg) and shall be composed of lead alloy with not less than 7.75 percent antimony by weight. Closet screws and bolts shall be of brass. Flanges shall be secured to the building structure with corrosion-resistant screws or bolts.

P3003.19.2 Securing floor and outlet fixtures. Add to read as shown.

P3003.19.2 Securing floor and outlet fixtures. Floor outlet fixtures shall be secured to the floor or floor flanges by screws or bolts of corrosion-resistant material.

Chapter 31, Vents

Section P3103 Vent Terminals

P3103.1 Roof extension.  Change to read as shown.

P3103.1 Roof extension. All open vent pipes which extend through a roof shall be terminated at least 6 inches (152 mm) above the roof except that where a roof is to be used for any purpose other than weather protection, the vent extensions shall be run at least 7 feet (2134 mm) above the roof.

P3103.2 Freezing.  Change to read as shown.

P3103.2 Freezing. Where the design temperature is less than 32° F (0°C), a water, soil or waste pipe shall not be installed outside of a building, in attics or crawl spaces, or be concealed in outside walls in any location subjected to freezing temperatures, unless adequate provision is made to protect them from freezing by insulation or heat or both. Water service pipe shall be installed not less than 12 inches (305 mm) deep or less than 6 inches (152 mm) below the frost line.

Chapter 32, Traps [No change.]

Part VIII Electrical

Chapter 34, General Requirements. Reserved

Section E3401 General

E3401.1 Applicability.  Change to read as shown.

E3401.1 Applicability. The provisions of NFPA 70, National Electrical Code  Requirements  shall establish the general scope of the electrical system and equipment requirements of this code.

Section E3402 Building Structure Protection

E3402 Bonding Metal Framing Members.  Change to read as shown.

E3402.1 Bonding Metal Framing Members.  Metal framing members. Metal framing members shall be bonded to the equipment grounding conductor for the circuit that may energize the framing and be sized in accordance with the National Electric Code Table 250.122. For the purpose of this section, a grounded metal outlet box attached to the framing shall be permitted.

Section E3403Cross references.  Change to read as shown.

Section E3403 Cross references.

E33031.  Add to read as shown.

E3303.1 See Table E3403, Cross References Defining Electrical Requirements of the Florida Building code.

Table E3403 Cross References Defining Electrical Requirements of the Florida Building Code.

Add to read as shown.

Table E3403 Cross references Defining Electrical Requirements of the Florida Building Code. [add Table from the 2007 FBC]

Section E3404 revise text to read as follows:

Section 3404 GFCI Protection

3404.1 NFPA 70 - 08: National Electric Code, Article 680 (Swimming Pools, Fountains, and Similar Installation), Section 680.22(B), GFCI Protection, is amended to read as follows:

(B)  GFCI Protection.  Outlets supplying pool pump motors from branch circuits with short-circuit and ground-fault protection rated 15 or 20 amperes, 125 volt or 240 volt, single phase, whether by receptacle or direct connection, shall be provided with ground-fault circuit-interrupter protection for personnel.

Exception: One-and two-family dwellings.

Section E3404.2 – E3404.12.  Reserved.

Section E3405 Equipment Location and Clearances.  Change to read as shown.

Section E3405 Equipment Location and Clearances.  Reserved.

Section E3406 Electrical Conductors and Connections.  Change to read as shown.

Section E3406 Electrical Conductors and Connections.  Reserved.

Section E3407 Conductor and Terminal Identification.  Change to read as shown.

Section E3407 Conductor and Terminal Identification. Reserved.

Chapter 35   Electrical Definitions.  Change to read as shown.

Chapter 35   Electrical Definitions.  Reserved

Chapter 36   Services.  Change to read as shown.

Chapter 36   Services.  Reserved

Chapter 37   Branch Circuit and Feeder Requirements.  Change to read as shown.

Chapter 37   Branch Circuit and Feeder Requirements.  Reserved

Chapter 38   Wiring Methods.  Change to read as shown

Chapter 38   Wiring Methods.  Reserved

Chapter 39 Power And Lighting Distribution.  Change to read as shown

Chapter 39  Power And Lighting Distribution.  Reserved

Chapter 40 Devices and Luminaires.  Change to read as shown

Chapter 40 Devices and Luminaires.  Reserved

Chapter 41 Appliance Installation.  Change to read as shown

Chapter 41 Appliance Installation.  Reserved

Chapter 42 Swimming Pools.  Change to read as shown

Chapter 42 Swimming Pools.  [Insert Chapter 41 from the 2007 Florida Building Code, Residential]

Section E4201 General.  Change to read as shown.

Section E4201 General.  Reserved.

Section E4202 Wiring Methods for Pools, Spas, Hot Tubs and Hydromassage Bathtubs.  Change to read as shown.

Section E4202 Wiring Methods for Pools, Spas, Hot Tubs and Hydromassage Bathtubs.  Reserved.

Section E4203 Equipment Location and Clearances.  Change to read as shown.

Section E4203 Equipment Location and Clearances.  Reserved.

Section E4204 Bonding  Change to read as shown.

Section E4204 Bonding  Reserved.

Section E4205 Grounding  Change to read as shown.

Section E4205 Grounding  Reserved.

Section E4206 Equipment Installation  Change to read as shown.

Section E4206 Equipment Installation  Reserved.

Section E4207 Storable Swimming Pools  Change to read as shown.

Section E4207 Storable Swimming Pools  Reserved.

Section E4208 Spas and Hot Tubs  Change to read as shown.

Section E4208 Spas and Hot Tubs  Reserved.

Section E4209 Hydromassage Bathtubs  Change to read as shown.

Section E4209 Hydromassage Bathtubs  Reserved.

Chapter 43 Class 2 Remote-Control, signaling and Power-Limited Circuits.

Chapter 423Class 2 Remote-Control, signaling and Power-Limited Circuits.  Change to read as shown.

Chapter 43 Class 2 Remote-Control, signaling and Power-Limited Circuits. Revise to read as follows:

Part IX – Referenced Standards

Chapter 43 Referenced Standards

Add or Revise the following standards as shown:

AA            Aluminum Association

900 19th Street N.W., Suite 300

Washington, DC 20006

Standard                                                                                                              Referenced in code

reference number    Title                                                                                           section number

ADM 1—00    Aluminum Design Manual, Specifications for Aluminum Structures, Allowable

Stress Design, Building Load and Resistance Factor Design, Commentary on

Allowable Stress Design,  Commentary on Building Load and Resistance Factor,

Material Properties, Design Aids and Illustrative Examples of Design	          R4406.1.2

AAF              Aluminum Association of Florida, Inc.

3165 McCrory Place, Suite 185

Orlando, FL 32803

Standard                                                                                                              Referenced in code

reference number    Title                                                                                           section number

AAF-  07-1  Guide to Aluminum Construction in High Wind Areas  2007-1  R301.2.1.1

AAMA       American Architectural Manufacturers Association

1827 Walden Office Square, Suite 550

## Schaumburg, IL 60173

Standard                                                                                                              Referenced in code

reference number    Title                                                                                           section number

101/I.S2—97      Voluntary Specifications for Aluminum, Vinyl (PVC) and Wood                 R613.3.3.1, R613.3.3.2,

Windows and Glass Doors	                                                                                            R4410.2.3.2.1

101/I.S2/NAFS—02  Voluntary Performance Specification for Windows, Skylights      R308.6.9, R613.3.1, 613.3.2,

and Glass Doors	                                                                                        R4410.2.3.2.1, R4412.1.2

AAMA/WDMA/CSA  North American Fenestration Standards/ Specifications for Windows, Doors and Skylights

101/I.S. 2/A440-05  08                                                                    R613.3.1, R613.3.2, R4410.2.3.2.1, N1106.AB.1.1

203-98                 Procedural Guide for the Window Inspection and Notification System                        R4410.2.3.2.6

450-06                 Voluntary Performance Rating Method for Mulled Fenestration

Assemblies                                                                                     R613.7.1, R613.7.1.2, R613.7.1.3

501—94               Methods of Test for Exterior Walls	                                                                              R4410.2.3.2.1

506-06                 Voluntary Specifications for Hurricane Impact and Cycle Testing of

Fenestration Products                                                                                                         R301.2.1.2

- 800—05 Voluntary Specifications and Test Methods for Sealants …… R613.8.1

812-04 Voluntary Practice for Assessment of Single Component Aerosol Expanding Polyurethane Foams for Sealing Rough Openings of Fenestration Installations 	 R613.8.1

  - Voluntary Specifications for Forced-entry Resistant Aluminum Prime

Windows	                                                                                                          R4410.2.3.2.1

1402-86               Standard Specifications for Aluminum Siding, Soffit and Fascia                                       R703.12.3

1600/I.S. 7-00      Voluntary Specifications for Skylights	                                                                     R4412.1.2

AAMA/NPEA/NSA 2100-02         Voluntary Specifications for Sunrooms                                               R301.2.1.1.2

ACCA	Air Conditioning Contractors of America

2800 Shirlington Road, Suite 300

Arlington, VA 22206

Standard reference number	Title	Referenced in Code Section Number

ACCA Manual D-1995 Residential Duct Systems                                                  N1110.AB.1

ACCA Manual J-2003 Residential Load Calculation, Eighth Edition with posted updates/errata N1107.AB.1

301 Specifications for Structural Concrete for Buildings                                       R4405.2.2

ACI           American Concrete Institute

38800 Country Club Drive

Farmington Hills, MI 48331

Standard                                                                                                              Referenced in code

reference number    Title                                                                                           section number

117                        Standard Tolerances for Concrete Construction and Materials	                                        R4405.2.2

301                        Specifications for Structural Concrete for Buildings	                                                       R4405.2.2

315                        Manual of Standard Practice for Detailing Reinforced Concrete Structures                     R4405.2.2

318-05 Building Code Requirements for Structural Concrete. . . . . . . . . . . . . R402.2, R404.1, Table R404.1.1(5), R404.4, R404.4.6.1, Table R404.4(1), Table R404.4(2), Table R404.4(3), Table R404.4(4), Table R404.4(5), R611.1, Table R611.3(1), Table R611.7(1), Table R611.7(2), Table R611.7(3), Table R611.7(4), Table R611.7(5), Table R611.7(6), Table R611.7(7), Table R611.7(9), Table R611.7(10), R611.7.1.1, Table R611.7.4, R612.1, R4405.8.5.5

347                        Recommended Practice for Concrete Formwork	                                 R4405.2.2, R4405.7.1.1

506                        Recommended Practice for Shotcreting	                                                                     R4405.2.2

506.2                     Building Code Requirements for Masonry Structures	       R4405.2.2, R4405.11.1.2, R4405.11.8.1

530/530.1-05         Building Code Requirements for Masonry Structures and Specifications               R404.1, R606.1,

for Masonry Structures & Commentaries	                                  R606.1.1, R4403.7.8, R4407.5.1

ADC	Air Diffusion Council

1000 E. Woodfield Rd., Suite 102

Schaumburg, IL 60173-5921

Standard reference number	Title				Referenced in Code Section Number

ADC 2003 Flexible Duct Performance & Installation Standards, Fourth Edition N1110.AB.2.2

AFPA           American Forest and Paper Association (American Wood Council Division)

111 19th Street, NW, #800

Washington, DC 20036

Standard                                                                                                            Referenced in code

reference number    Title                                                                                        section number

NDS—05	National Design Specification (NDS) for Wood Construction with                      R404.2.2, R502.2,

2001 Supplement	                                                      Table R503.1, R602.2, R802.2, R4404.7.1.8.1,

R4409.1.4.7, R4409.2.4.1, R4409.6.17.2.1.3, R4409.6.17.2.1.3, R4409.6.17.2.1.5

AFPA—01	Design Values for Wood Construction	                       R4409.1.4.7, R4409.6.17.2.2.1

AFPA—87	All-Weather Wood Foundation System, Design, Fabrication, Installation Manual         R4409.1.4.7

AFPA—92	Wood Structural Design Data		                                                                  R4409.1.4.7

AFPA—93?	Working stresses for Joists and Rafters		                                                    R4409.1.4.7

AFPA—93	Span Tables for Joists and Rafters	         R502.2.2, R802.2.2, R802.2.3, R4409.1.4.7, R4409.4.1.1

T.R. No. 7—87	Basic Requirements for Permanent Wood Foundation System	           R401.1, R4409.1.4.7

WCD 1—01	Wood Construction Data No. 1, Details for Conventional Wood Frame Construction   R4409.1.4.7

WCD 4—03	Wood Construction Data number 4, Plank and Beam Framing for Residential Building 4409.1.4.7

WCD 5—04	Wood Construction Data No. 5, Heavy Timber Construction Details		         R4409.1.4.7

WCD 6—01	Wood Construction Data No.6, Design of Wood Frame structures for Permanence      R4409.1.4.7,

R4409.13.2.11

WFCM—01 08	Wood Frame Construction Manual for One- and Two-family Dwellings	       R301.2.1.1, R404.1.4,

R614.2.5, R614.3.1, R802.2, R4409.1.4.7

AHA	American Hardboard Association

1210 West Northwest Highway

Palatine, IL 60067

Standard                                                                                                              Referenced in code

reference number    Title                                                                                           section number

A135.4—04	Basic Hardboard		                                                                   Table R602.2(1), R4409.1.4.1

A135.5—04	Prefinished Hardboard Paneling		                                                     R702.5, R4409.1.4.1

A135.6—98	Hardboard Siding		                                                                       Table R703.4, R4409.1.4.1

IB Spec. No. 1	Recommended Product and Application Specification-Structural

Insulating Roof Deck		                                                                                 R4409.1.4.1

IB Spec. No. 2	Recommended Product and Application Specification-½ inch

Fiberboard Nail-Base Sheathing		                                                                  R4409.1.4.1

IB Spec. No. 3	Recommended Product and Application Specification-½ inch

Intermediate Fiberboard Sheathing	                                                                                 R4409.1.4.1

AHAM	Association of Home Appliance Manufacturers

20 North Wacker Dr.

Chicago, IL 60606

Standard reference number	Title				Referenced in Code Section Number

ANSI/AHAM RAC1-03 Room Air Conditioners                                         Table 1107.AB.3.2D

AHRI  (Formerly ARI)

Air-Conditioning Heating and Refrigeration Institute

Suite 500

2111 Wilson Boulevard

Arlington, VA 22201

Standard reference number Title                                            Referenced in code section number

ARI Std. 210/240-2006 Unitary Air-Conditioning and Air-Source Heat Pump Equipment

Tables N1107.AB.3.2A, N1107.AB.3.2B

ARI Std. 310/380-2004 Packaged Terminal Air-Conditioners and Heat Pumps

Tables N1107.AB.3.2D

ARI Std. 340/360-2004 Commercial and Industrial Unitary Air-Conditioning and Heat Pump Equipment                                                               Tables N1107.AB.3.2A, N1107.AB.3.2B

ARI Std. 365-2002 Commercial and Industrial Unitary Air-Conditioning Condensing Units

Table N1107.AB.3.2A

ARI Std. 390-2003 Single Packaged Vertical Air Conditioners and Heat Pumps

Table N1107.AB.3.2D

ARI Std. 1160-2004 Performance Rating of Heat Pump Pool Heaters               N1112.AB.2.3.4

AISC       American Institute of Steel Construction

One East Wacker Drive Suite 3100

Chicago, IL 60601-2001

Standard                                                                                                              Referenced in code

reference number    Title                                                                                           section number

AISC                     Detailing for Steel Construction	                                                                                    R4408.1.3

AISC                     Engineering for Steel Construction	                                                                                    R4408.1.3

AISC                      Iron and Steel Beams 1873 to 1952	                                                                     R4408.1.3

AISC                      Plastic Design in Steel	                                                                                                  R4408.1.3

AISC                      Plastic Design of Braced Multistory Steel Frames	                                                       R4408.1.3

AISC                      Serviceability Design Considerations for Low Rise Buildings	                                        R4408.1.3

AISC                      Simple Shear Connection, ASD	                                                                                    R4408.1.3

AISC                      Simple Shear Connection, LRFD	                                                                                    R4408.1.3

AISC                     Torsional Analysis of Steel Members	                                                                     R4408.1.3

AISC                      Manual of Steel Construction, Allowable Stress Design                                                  R4408.1.3

AISC                      Manual of Steel Construction, Allowable Stress Design LRFD                                       R4408.1.3

AISI            American Iron and Steel Institute

1140 Connecticut Ave, Suite 705

Washington, DC 20036

Standard                                                                                                              Referenced in code

reference number    Title                                                                                           section number

AISI                  Design Manual for Structural Tubing	                                                                                    R4408.1.3

AISI                  Designing Fire Protection for Steel Trusses	                                                                     R4408.1.3

AISI                  Designing Fire Protection for Steel Columns	                                                                     R4408.1.3

AISI                  Fire Resistant Steel Frame Construction	                                                                     R4408.1.3

AISI                  Fire Safe Structural Steel A Design	                                                                                    R4408.1.3

AISI                   Specifications for Design of Light Gage Cold Formed Stainless Structural Members         R4408.1.3

AISI                   Specification for the Criteria for Structural Application of Steel Cables for Buildings        R4408.1.3

AISI/COFS/PM-2001  Standard for Cold formed Steel Framing-- Prescriptive Method                R301.1, R301.2.1.1,

S230-07               for One- and Two- family dwellings	         R301.2.2.4.1, R301.2.2.4.5, R404.1.4, R804.1.3

AISI/COFS/PM Supplement 2004                                                                                                                  R404.1.4.2

SGO4-5             Standard for Cold formed Steel Framing Truss Design	                                                         R804.1.3

SGO4-6             Standard for Cold formed Steel Framing Header Design                                                       R603.6

SGO3-3             Cold Formed Steel Design Manual	                                                                                    R4408.1.3

SG 971—96       Specification for the Design of Cold Form Steel Structures	                                        R4408.1.3

AITC         American Institute of Timber Construction

7012 S. Revere Parkway, Suite 140

Englewood, CO 80112

Standard                                                                                                              Referenced in code

reference number    Title                                                                                           section number

AITC 104             Typical Construction Details	                                                                                 R4408.1.4.2

AITC 106             Code of Suggested Practices	                                                                                 R4409.1.4.2

AITC 108             Standard for Heavy Timber Construction	                                                                  R4409.1.4.2

AITC 109             Standard for Preservative Treatment for Structural Glued Laminated Timber                R4409.1.4.2

AITC 110             Standard Appearance Grades for Structural Glued Laminate Timber	                       R4409.1.4.2

AITC 112             Standard for Torque and Groove Heavy Timber Roof Decking	                                     R4409.1.4.2

AITC 113             Standard for Dimensions of Glued Laminated Structural Members	                       R4409.1.4.2

AITC 117             Standard Specification for Structural Glued Laminated Timber of Softwood Species   R4409.1.4.2

AITC 119             Standard Specifications for Hardwood Glued Laminated Timber	                       R4409.1.4.2

AITC A 190.1—02 07 Structural Glued Laminated Timber  R502.1.1.5, R602.1.1.2, R802.1.5, R4409.1.4.2, R4409.2.11

TR No. 7               Calculation of Fire Resistance of Glued Laminated Timber	                                     R4409.1.4.2

ANSI        American National Standards Institute

25 West 43rd Street, Fourth Floor

New York, NY 10036

Standard                                                                                                              Referenced in code

reference number    Title                                                                                           section number

A41.1                 Building Code Requirements for Masonry	                                             R4407.2.1.1, R4407.4.2.8

A41.2                 Building Code Requirements for Reinforced Masonry	                                                    R4407.2.1.1

A42.1                 Standard Specification for Gypsum Plastering	                                                                  R4411.2.1.1

A42.4                 Standard Specification for Interior Lathing and Furring	                                                          R4411.1

A97.1                 Specification for the Application and Finishing of Gypsum Wallboard	                          R4411.4.2

A112.18.1M-99 Finished and Rough Brass Plumbing Fixture Fittings      N1108.A.3.5, N1112.AB.2.4

ANSI Z21.10.3-2004	Gas Water Heater, Volume 3, Storage, with Input Ratings above      N1112.AB.3.1.2,

75,000 Btu/h, Circulating and Instantaneous Water Heaters	      Appendix G C4.3.1.3

ANSI Z21.40.4-96(with Addenda 1)  Performance Testing and Rating of Gas-Fired,

Air-Conditioning and Heat Pump Appliances 		   N1107.A.1

ANSI Z21.47a-04 Gas-Fired Central Furnaces                                           Table N1108.AB.3.2E

ANSI Z21.56-2006 Gas-Fired Pool Heaters                                                        N1112.AB.2.3.1

Z83.8/CGA 2.6-06 Gas Unit Heaters and Gas-Fired Duct Furnaces Table N1108.AB.3.2E

Z21.83—98            Fuel Cell Power Plants	                                                                                                    M1903.1

Z97.1—84(R1994) 04  Safety Glazing Materials Used in Buildings—Safety Performance

Specifications and Methods of Test (Reaffirmed 1994)	                    R308.3, R4403.7.3.6.3,

R4410.2.1.4, R4410.2.1.6

APA                     APA The Engineered Wood Association

7011 South 19th

Tacoma, WA 98466

Standard                                                                                                              Referenced in code

reference number    Title                                                                                           section number

V910               Plywood Folded Plate, Laboratory Report 21	                                                                  R4409.1.4.3

L350               Design/Construction Guide Diaphragms	                                                                  R4409.1.4.3

PRP108           Performance Standards and Policies for Structural Use Panels	                R4409.1.4.3, R4409.2.1.2

B840               303 Siding Manufacturing Specifications	                                                                  R4409.1.4.3

E30—03         Engineered Wood Construction Guide	                                                                R803.2.3, R4409.1.4.3

H815               Plywood Design Specification Design and Fabrication of All Plywood Beams                   R4409.1.4.3

S811                Plywood Design Specification Design and Fabrication of Plywood Curved Panels	         R4409.1.4.3

S812                Plywood Design Specification Design and Fabrication of Plywood Lumber Beams          R4409.1.4.3

U813               Plywood Design Specification Design and Fabrication of Plywood Stressed Skin Panels  R4409.1.4.3

U814               Plywood Design Specification Design and Fabrication of Plywood Sandwich Panels        R4409.1.4.3

Y510J              Plywood Design Specification	                                                                                 R4409.1.4.3

APSP

Association of Pool and Spa Professionals

ANSI/APSP 7—06 American National Standard for Suction Entrapment Avoidance in Swimming Pools, Wading Pools, Spas, Hot Tubs, and Catch Basins…………….……………………………….R4101.6.1, R4101.6.3, R4101.6.6

ANSI/NSPI 3—99 American National Standard for Permanently Installed Residential Spas……………………………………………………………R4101.6.1

ANSI/NSPI 4—99 American National Standard for Aboveground/On ground Residential Swimming Pools……………………………………………..R4101.6.1

ANSI/NSPI 5—03 American National Standard for Residential In ground Swimming Pools…………………………………………………………….R4101.6.1

ANSI/NSPI 6—99 American National Standard for Portable Spas…………………………………………………………………………...R4101.6.1

ARDM	Association of Refrigerant Desuperheater Manufacturers, Inc,

c/o Doucette Industries

4151 112 Terrace N

Clearwater, FL 33762

Standard reference number	Title	Referenced in Code Section Number

ARDM-88	Residential Heat Recovery Installation Guide, First Edition		N1100.3.3

ASCE          American Society of Civil Engineers

1801 Alexander Bell Drive

Reston, VA 20191-4400

Standard                                                                                                              Referenced in code

reference number    Title                                                                                           section number

3—91         Specifications for the Design and Construction of Composite Slabs and Commentary

on Specifications for the Design and Construction of Composite Slabs                     R4405.2.3, R4408.1.3

5—05 08   Building Code Requirements for Masonry Structures      R404.1, R606.1, R606.1.1, R606.2.2, R606.11.1,

R606.11.2.2.1, R606.11.2.2.2, R606.11.3.1, R4403.7.8

7—05        Minimum Design Loads for Buildings and Other Structures     Figure 301.2(4), R301.2.1.1, R301.2.1.1.2,

R301.2.1.4, Table R611.3(1), Table R611.7.4, R4402.3.4, R4403.1.3, R4403.4.1, R4403.4.2,

R4403.7.3.8, R4403.7.8, R4403.8, R4403.9, R4403.10, R4403.12, Table R4403.15.4, R4403.16.1

8—02        Specifications for the Design of Cold Formed Stainless Steel Structural members             R4408.1.3

11—99      Guidelines for Structural Condition Assessment of	Existing Buildings  R4405.2.3, R4406.1.2, R4408.1.3

32—01      Design and Construction of Frost Protected Shallow Foundations	                     R403.1.4.1, R4406.1.2

ASHRAE            American Society of Heating, Refrigerating and Air Conditioning Engineers, Inc.

1791 Tullie Circle, NE

Atlanta, GA 30329

Standard                                                                                                              Referenced in code

reference number    Title                                                                                           section number

34—2004                Designation and Safety Classification of Refrigerants	                                          M1411.1

ANSI/ASHRAE Std. 93-1986 (RA91) Methods of Testing to Determine the Thermal Performance of Solar Collectors                                                                   N1112.AB.3.4

ANSI/ASHRAE 119-1988		Air Leakage Performance for Detached Single-Family

(RA 94)				Residential Buildings					Table N1113A.1-1

ANSI/ASHRAE 124-1991		Methods of Testing for Rating Combination Space-Heating

and Water-Heating Appliances 		N1108.A.2.5, Appendix G C4.3.2.1

ANSI/ASHRAE 137-1995 (RA2001)Methods of Testing for Efficiency of Space-conditioning/ Water-Heating

Appliances That Include a Desuperheater Water Heater	Appendix G C6.2.2.3

ANSI/ASHRAE 152-2004      	Method of Test for Determining the Design and Seasonal	 N1110.A.2

Efficiencies of Residential Thermal Distribution Systems	Table N1113A.1-1

ASHRAE, 1998 Cooling and Heating Load Calculation Principles            N1107.AB.1

ASHRAE—2005    ASHRAE Fundamentals Handbook          N1100.7.3, Table N1113A.1-1,  P3001.2, P3002.3, P3101.4, P3103.2

ASME                American Society of Mechanical Engineers

Three Park Avenue

New York, NY 10016-5990

Standard                                                                                                              Referenced in code

reference number    Title                                                                                           section number

B16.3—1999 2006     Malleable Iron Threaded Fittings Classes 150 and 300	     Table P2904.6, Table R4413.2.7

B16.4—1998  2006     Gray iron Threaded Fittings Classes 125 and 250	     Table P2904.6, Table R4413.2.7

B16.9—2003               Factory made Wrought Steel Buttwelding Fittings	     Table P2904.6, Table R4413.2.7

B16.11—2001 2005    Forged Fittings, Socket welding and Threaded	                   Table P2904.6, Table R4413.2.7

B16.12—1998             Cast Iron Threaded Drainage Fittings	                                  Table P2904.6, Table R4413.2.7

B16.15—1985(R1994) 2006 Cast Bronze Threaded Fittings	                                  Table P2904.6, Table R4413.2.7

B16.18—2001 (R2005)  Cast Copper Alloy Solder Joint Pressure Fittings      Table P2904.6, Table R4413.2.7

B16.22—2001  (R2005)  Wrought Copper and Copper Alloy Solder Joint Pressure Fittings   Table P2904.6, Table R4413.2.7

B16.23—2002  (R2006)  Cast Copper Alloy Solder Joint Drainage Fittings (DWV) Table P2904.6, Table R4413.2.7

B16.26—1988 2006  Cast Copper Alloy Fittings for Flared Copper Tubes	     Table P2904.6, Table R4413.2.7

B16.28—1994   Wrought Steel Buttwelding Short Radius Elbows and Returns	     Table P2904.6, Table R4413.2.7

B16.29—2001   Wrought Copper and Wrought Copper Alloy Solder Joint Drainage

Fittings DWV	                                                                             Table P2904.6, Table R4413.2.7

B16.32               Cast Copper Alloy Solder Joint Fittings for Solvent Drainage Systems	                Table R4413.2.7

BPVC-2004 ASME Boiler and Pressure Vessel Code  (Sections I,II, IV, V, VI & IX)                                                                                                              M2001.1.1, G2452.1

ASTM              ASTM International

100 Barr Harbor Drive

West Conshohocken, PA 19428

Standard                                                                                                              Referenced in code

reference number    Title                                                                                           section number

A 6/A6M—04a       Specification for General Requirements for Rolled Structural Steel Bars,

Plates, Shapes and Sheet Piling	                                                                                    R4408.1.3

A 29/A29M             Specification for Steel bars, Carbon and Alloy, Hot Wrought, General

Requirements	                                                                                                              R4404.11.1

A 53/A53M—02 06a Specification for Pipe, Steel, Black and Hot dipped, Zinc Coated Table 2904.4.1

Welded and Seamless Table M2101.1, Table P2904.5, Table P3002.1, G2414.4.2, Table R4413.2.2

A 74—04 06            Specification for Cast Iron Soil Pipe and Fittings	                       Table P3002.1,Table P3002.2,

Table R4413.2.2, Table R4413.2.3, Table R4413.2.4, Table R4413.2.5

A 82—02                 Specification for Steel Wire, Plain for Concrete Reinforcement	                          R606.9.10

A 306                        Carbon Steel Bars Subject to Mechanical Property Requirements	                        R4404.11.1

A 307—03                Specification for Carbon Steel Bolts and Studs 60,000 PSI Tensile Strength	       Table R611.9

A 325—94                Specification for High Strength Bolts for Structural Steel Joints                           R4408.1.3

A 361                        Specification for Steel Sheet Zinc Coated (Withdrawn)	                                R4409.6.17.1.1

A 416 99                   Specification for Steel Strand, Uncoated Seven Wire for Prestressed Concrete	         R4405.4.4.2

A 421/A421M—98   Specification for Uncoated Stress Relieved Steel Wire for Prestressed Concrete      R4405.4.4.2

A 446                        Specification for Steel Sheet, Zinc Coated (Galvanized) by the Hot Dip

Process, Structural (Physical) Quality	                                                                R4405.12.4.4

A463/A463M-02a  05	???

A 490—93                Specification for Heat Treated Steel Structural Bolts	                                        R4408.1.3

A 525 87              Specification for Steel Sheet Zinc coated (Galvanized) Steel Wire  Table R606.9.10.1,

R4405.12.4.4, R4408.1.3, R4411.4.2, R4411.4.5.1, R4411.4.5.4, M1601.1.1

A 611                    Standard Specification for Structural Steel (SS), Sheet, Carbon, Coil Rolled    R4404.10.1.5.3,

R4405.12.4.4

A 615/A 615M-04a Specification for Deformed and Plain Billet Steel Bars for Concrete

Reinforcement	                                                                        R4405.2.2, R4405.2.4, R4405.4.4.6

A 617                      Standard Specification for Axle Steel Reformed and Plain Bars for

Concrete Reinforcement	                                                                                               R4405.4.4.6

A 653/A 653M-04  Specification for Steel Sheet, Zinc Coated (Galvanized) or Zinc Iron             R505.2.1, R505.2.3,

07    Alloy Coated (Galvanized) by the Hot Dip Process	      R603.2.1, R603.2.3, R804.2.1, R804.2.3,

Table 905.4.4, Table R905.10.3, R4409.6.17.2.2.7

A 706/A 706M-04a  Specification for Low Alloy Steel Deformed and Plain Bars for

05a      Concrete Reinforcement	                                               R404.4.6.1, R611.6.2, R4405.4.4

A 722/A 722M-98  Specification for Uncoated High Strength Steel Bar for Prestressing Concrete          R4405.4.4.2

A 767/A 767M-00b Specification for Zinc Coated (Galvanized) Steel Bars for Concrete

Reinforcement	                                                                                        R4405.4.4.6, R4405.8.5.5

A 775/A 775M-01   Specification for Epoxy Coated Steel Reinforcing Bars	                                     R4405.4.4.6

A 888-04 07a           Specification for Hubless Cast Iron Soil Pipe and Fittings for      Table P3002.1, Table P3002.2,

Sanitary And Storm Drain, Waste, and Vent Piping Application                        Table R4413.2.2,

Table R4413.2.3, Table R4413.2.4, Table R4413.2.5, Table R4413.2.7

A 924/A924M-04   Standard Specification for General Requirements for Steel Sheet, Metallic

07    Coated by the Hot Dip Process	                                                                         R4409.6.17.2.2.7

B 43—98 (2004)       Specification for Seamless Red Brass Pipe, Standard Sizes	            Table M2101.1, G2413.5.2,

Table P3002.1, Table P2904.4.1Table P2904.5, Table R4413.2.2

B 75—03 02        Specification for Seamless Copper Tube	       Table M2101.1, Table P2904.4.1, Table P2904.5,

Table P3002.1, Table P3002.2, Table R4413.2.2, Table R4413.2.3, Table R4413.2.4

B 88—02  03     Specification for Seamless Copper Water TubeTable M2101.1, G2414.5.2, Table P2904.4.1,

Table P2904.5, Table P3002.1, Table P3002.2, Table R4413.2.2, Table R4413.2.3, Table R4413.2.4

B 227—04        Specification for Hard drawn Copper clad Steel Wire	                                                       R606.9.10

B 251—02e01  Specification for General Requirements for Wrought Seamless Copper and Copper   Table M2101.1,

alloy Tube      Table P2904.4.1, Table P2904.5, Table R4413.2.2, Table R4413.2.3, Table R4413.2.4

B 302—02   Specification for Threadless Copper Pipe, Standard Sizes	                  Table M2101.1, Table P2904.4.1,

Table P2904.5, P2904.4, Table R4413.2.2

B 306—02    Specification for Copper Drainage Tube (DWV)	          Table M2101.1, Table P3002.1, Table P3002.2,

Table R4413.2.2, Table R4413.2.4

B 370—03    Specification for Copper Sheet and Strip for Building Construction	                                Table R905.4.4

Table R905.10.3, Table P2701.1

B695-00  04

C4—03  04e01 Specification for Clay Drain Tile and Perforated Clay Drain Tile  Table R4413.2.4, Table R4413.2.5

C5—03     Specification for Quicklime for Structural Purposes	                                      R702.2, R4411.2.2.3

C 14—03 07  Specification for Concrete Sewer, Storm Drain, and Culvert Pipe     Table P3002.2, Table R4413.2.4

C 28/C28M-00e01 00(2005) Specification for Gypsum Plasters                                                    R702.2, R4411.2.2.2

C 31/C 31M-98Practice for Making and Curing Concrete Test Specimens in the Field  R4405.5.2.2.3, R4405.5.2.3.2

C 33—01a  03      Specification for Concrete Aggregates	                                                R4405.4.2, R4405.4.2.2

C 34-03  Specification for Structural Clay Load bearing Wall Tile	      Table R301.2(1), R4407.2.8.3.1

C 35-9501(20015)  Specification for Inorganic Aggregates for Use in Gypsum Plaster        R702.2, R4411.2.2.1.1

C 36/C 36M-03 Specification for Gypsum Wallboard	                                   R702.3.1, N1100.7,  R4411.4.2

C 37/C 37M-01 Specification for Gypsum Lath	                                                                      R702.2, R4411.1.2

C 39—99ael      Test Method for Compressive Strength of Cylindrical Concrete Specimens	      R4405.5.2.2.3

C 42/C 42M-99 Test Method for Obtaining and Testing Drilled Cores and Sawed Beams of Concrete     R4405.5.2.4

C 52                   Specification for Gypsum Partition Tile or Block	                                                    R4407.2.9.3

C 55—03 06e01   Specification for Concrete Brick              R202, Table R301.2(1), R4407.2.4.2.2, R4407.2.4.3.3

C 56-96 (2001)  Specification for Structural Clay Nonload Bearing Tile	                                                 R4407.2.8.3.3

C 57                   Specification for Structural Clay Floor Tile	                                                               R4407.2.8.3.2

C 59/C 59M-00 (2006)    Specification for Gypsum Casting and Molding Plaster	                                             R702.2

C 61/C 61M-00  (2006)    Specification for Gypsum Keene’s Cement	                   R702.2, R4411.1.2, R4411.2.2.4

C 62—04  05         Specification for Building Brick (Solid Masonry Units Made from Clay or Shale)                R202,

C 67—03ae01         Test Methods of Sampling and Testing Brick and Structural Clay Tile	      R905.3.5, R4407.2.4.2

C 76—04a  07         Specification for Reinforced Concrete Culver, storm Drain and Sewer Pipe	  Table R4413.2.4

C 90—03              Specification for Load Bearing Concrete Masonry Units     Table R301.2(1), R606.4, R4407.2.7.2

C 91—01 05             Specification for Masonry Cement                                                                              R4412.2.2.6

C 94                      Specification for Ready Mixed Concrete	                                                                     R4405.6.2

C 144—03            Standard Specification for Aggregate for Masonry Mortar	         R4405.10.7.2, R4407.2.12.1.1

C 150—02ael  07      Specification for Portland Cement                                                        R4405.4.1, R4412.2.2.5.1

C 172—99             Practice for Sampling Freshly Mixed Concrete	                                                    R4405.2.2.2

C 177-04 Test Method for Steady-State Heat Flux Measurements and Thermal Transmission Properties by Means of the Guarded-Hot-Plate Apparatus            Table R301.2(1), N1110.AB.2.2

R4407.2.4.3.1

C 199-84(20005)    Test Method for Pier Test for Refractory Mortar	        R1001.9, R1003.5, R1003.8, R4405.4.1

C 206-84(1997)    Specification for Finishing Hydrated Lime	                                                                  R4411.2.2.3

C 212—00            Specification for Structural Clay Facing Tile	                                                    R4407.2.8.2

C 216—04a 07     Specification for Facing Brick (Solid Masonry Units Made from Clay or Shale)                    R202,

Table R301.2(1), R4407.2.4.3.1

C 236-89 (1993el)	Test Method For Steady-State Thermal Performance of Building

Assemblies by Means of a Guarded Hot Box.		Appendix G C2.2.2

C 270—04   07        Specification for Mortar for Unit Masonry	                                                   R607.1, R4407.2.12.1

C 330—99            Specification for Lightweight Aggregates for Structural Concrete	                          R4405.4.2

C 332—99            Standard Specification for Lightweight Aggregates for Insulation Concrete	       R4405.12.4.6

C 425-04              Specification for Compression Joints for Vitrified Clay Pipe and FittingsTable P3002.2, P3003.3.5

C 428-97(20026)   Specification for Asbestos Cement Nonpressure Sewer pipe	  Table R4413.2.3, Table R4413.2.4

C 471M-01      Standard Test Methods for Chemical Analysis of Gypsum and Gypsum Products            R4407.2.9.2,

R4407.2.9.3

C 472—99       Specification for Standard Test Methods for Physical Testing of Gypsum,

Gypsum Plasters and Gypsum Concrete	                                             R4407.2.9.2, R4407.2.9.3

C 473—00       Test Method for Physical Testing of Gypsum Panel Products	                R4407.2.9.2, R4407.2.9.3

C 475/C475M—02 Specification for Joint Compound and Joint Tape for Finishing Gypsum Wallboard     R702.3.1,

M-05                                                                                                                                                 R4411.4.2

C 494/C 494M-99 Standard Specification for Chemical Admixtures for Concrete                                   R4405.12.4.4

C 495-99a        Standard Test Method for Compressive Strength of Lightweight Insulating Concrete    R4405.12.1.1,

R4405.12.1.2, R4405.12.1.3

C 508—00 04      Specification for Asbestos Cement Underdrain Pipe	                                             Table R4413.2.5

C 516-02		Vermiculite Loose Fill Thermal Insulation			Appendix G Table B1.2.3

C 518-04 Test Method for Steady-State Thermal Transmission Properties by Means of the Heat Flow Meter Apparatus                                                                                       N1110.AB.2.2

C 549-06		Perlite Loose Fill Insulation				Appendix G Table B-1.2.3

C 578-06  07		Rigid, Cellular Polystyrene Thermal Insulation		Appendix G Table B-1.2.3

C 595—01 07       Specification for Blended Hydraulic Cement	                                                       R4405.4.1

C 618—99       Specification for Coal Fly Ash and Raw or Calcined Natural Pozzolar for Use

as a  Mineral Admixture in Concrete	                                                                               R4405.12.4.4

C 645—04 07      Specification for Nonstructural Steel Framing Members        R702.3.3, R4409.6.17.1.3, R4411.4.2,

R4411.4.5.1, R4411.4.5.4

C 652—04a    Specification for Hollow Brick (Hollow Masonry Units Made from Clay or Shale)                    R202,

05a                                                                                                                      Table R301.2(1), R4407.2.4.3.1

C 665-06		Mineral-Fiber Blanket Thermal Insulation for Light Frame

Construction and Manufactured Housing			Appendix G Table B-1.2.3

C 685/C 685M-98a 01 Specification for Concrete Made by Volumetric Batching and Continuous Mixing   R4405.6.2.2

C 700-02 07  Specification for Vitrified Clay Pipe, Extra Strength, Standard Strength, and Perforated Table P3002.2,

R4409.6.17.1.3, Table R4413.2.4, Table R4413.2.5

C 727-01		Standard Practice for Installation and Use of Reflective

Insulation in Building Constructions.			Appendix G Table B-1.2.3

C 739-05b	Cellulosic Fiber (Wood-Base) Loose-Fill Thermal Insulation	Appendix G Table B-1.2.3

C 764-06a	Mineral Fiber Loose-Fill Thermal Insulation			Appendix G Table B-1.2.3

C 794—01    Test Method for Adhesion in Peel of Elastometric Joint Sealants	                                        R4410.6.4

C 796—97    Standard Test Method for Foaming Agents for Use in  Producing Cellular Concrete

Using Performed Foam	                      R4405.12.1.1, R4405.12.1.2, R4405.12.1.3, R4405.12.4.6

C 869          Specification for Foaming Agents Used in Making Performed Foam for Cellular Concrete R4405.12.4.6

C 887-79(2001) 05 Specification for Packaged, Dry, Combined Materials for Surface Bonding Mortar           R406.1

C 920 - 05 Specification for Elastomeric Joint Sealants …………………... R4410.6.4, R613.8.1

C 926-98a  (2005)   Specification for Application of Portland Cement Based Plaster  R202, R703.6.2.1, R4411.3.1.1,

R4411.3.1.4

C 1015-06	Standard Practice for Installation of Cellulosic and Mineral Fiber

Loose-Fill Thermal Insulation				Appendix G Table B-1.2.3

C 1029-05a	Specification for Spray-Applied Rigid Cellular Polyurethane

Thermal Insulation					Appendix G Table B-1.2.3

C 1036-01     Specification for Flat Glass	                                                                                               R4410.2.1.2

C 1048-04     Specification for Heat Treated Flat Glass—Kind HS, Kind FT Coated 7 Uncoated Glass    R4410.2.1.5

C 1053-00     Specification for Borosilicate Glass Pipe and Fittings for Drain, waste and Vent

(DWV) Applications	                                                                                                      Table R4413.2.2

C 1077         Standard Practice for Laboratories Testing Concrete and Concrete Aggregates for

Use in Construction and Criteria for Laboratory Evaluation	                      R4405.2.4, R4405.4.6

C 1158-05	Standard Practice for Use and Installation of Radiant Barrier Systems	 N1104.A.3,

(RBS) in Building Construction		  		Appendix G Table B-1.2.3,

Appendix G Table C4.2.1.4

C 1224-03	Reflective Insulation for Building Applications		Appendix G Table B-1.2.3

C 1281- 03 Standard Specification for Preformed Tape Sealants for Glazing Applications ………………………………………..………… R613.8.1.8.1

ASTM C 1289-06 07	Faced Rigid Cellular Polyisocyanurate Thermal Insulation Board   Appendix G Table B-1.2.3

ASTM C 1313-05	Sheet Radiant Barriers for Building Construction Applications		N1104.A.3,

Appendix G Table B-1.2.3, Appendix G Table C4.2.1.4

ASTM C 1320-05	Standard Practice for Installation of Mineral Fiber Batt and

Blanket Thermal Insulation for Light-Frame Construction	Appendix G Table B-1.2.3

ASTM C 1321-04	Standard Practice for Installation and Use of Interior Radiation		 N1104.A.3

Control Coating Systems (IRCC) in Building Construction	Appendix G Table B-1.2.3

Appendix G Table C4.2.1.4

ASTM C 1371-04a	Test Method for Determination of Emittance of Materials Near     N1104.A.3, N1104.4

Room Temperature Using Portable Emissometers.		Appendix G Table B-1.2.3,

Appendix G Table C4.2.1.4

ASTM C 1549-04 	Standard Test Method for Determination of Solar Reflectance Near

Ambient Temperature Using a Portable Solar Reflector	N1104.A.4

D 25-99                      Standard Specification for Round Timber Piles	                                                       R4404.7.1

D 41-e01   05             Specification for Asphalt Primer Used in Roofing, Dampproofing,                    Table R905.9.2,

and Waterproofing   Table R905.11.2, R4402.3.2.3.2, R4402.6.6.2.4, R4402.8.6, R4402.10.6, R4402.10.14.1

D 43-00  (2006)                   Specification for Coal Tar Primer Used in Roofing, Damproofing and

Waterproofing	 Table R905.9.2, R4402.6.6.2.4, R4402.8.6, R4402.10.6, R4402.10.14.2

D 92                          Standard Test Method for Flash and Fire Points by Cleveland Open Cup          R4402.8.2.2

D 226-97a   06         Specification for Asphalt saturated (Organic Felt) Used in Roofing and           R703.2, R703.9.1,

Waterproofing	      R905.2.2, R905.2.3, R905.2.7, R905.4.3, R905.5.3, R905.6.3, R905.8.4,

R905.8.10.1, Table 905.9.2, R4402.7.4

D 256-03                  Test Methods for Determining Izod Pendulum Impact Resistance of Plastics	            R4412.1.2

D 312-00   (2006)     Specification for Asphalt Used in Roofing	            R905.9.2, R4402.8.4, R4402.10.14.1

D 412-98a(2002)el   Test Methods for Vulcanized Rubber and Thermoplastic Elastomers Tension	            R4410.6.4

D 624-00el                 Test Methods for Tear Strength of Conventional Vulcanized Rubber and

Thermoplastic Elastomers	                                                                                    R4410.6.4

D 635-03                    Test Methods for Rate of Burning and/or Extent & Time of Burning of Plastics

in a Horizontal Position	                                                                                    R4412.1.2

D 1079-02               Standard Terminology Relating to Roofing, Waterproofing and Bituminous Materials R4402.2.1

D 1143-81 (1994) e01  Test Method for Piles Under Static Axial Compressive Load                               R4404.13.1.7

D 1167                     Methods of Testing Asphalt Base Emulsions for Use as Protective

Coatings for Built Up Roofs	                                                                            R4402.12.6.5.2

D 1556                     Standard Test Method for Density of Soil In Place by the Sandcone	                       R4404.4.3.2

D 1557-00               Test Method for Laboratory Compaction Characteristics of Soil Using

99-(2005)                        Modified Effort [56,000 ft lb/ft3 (2700 kN m/m3)]	                      R4404.4.3.2

D 1586-99                Specification for Penetration Test and Split Barrel Sampling of Soils	                     R4404.18.3.3

D 1621                     Standard Test Method for Compressive Properties of Rigid Cellular Plastics 4402.12.6.5.2.17.1

D 1622   -03             Standard Test Method for Apparent Pensity of Rigid Cellular Plastics          R4402.12.6.5.2.17.2

D 1623 -78(1995)    Standard Test Method for Tensile and Tensile Adhesion Properties of

Rigid Cellular Plastics	                                                                                  R4402.12.6.5.2.17.3

D 1693-01 07           Test Method for Environmental Stress cracking of Ethylene Plastics	                  Table M2101.1

D 1760                     Standard Specification for Pressure Treatment of Timber Products	                   Table R4404.7

D 1761-88(2000)el  Test Methods for Mechanical Fasteners in Wood	                                                    R4409.1.4.4

D 1861                      Specification for Homogenous Bituminized Fiber Drain Sewer Pipe

(Withdrawn 1992—Replacement)	                                                                         P3002.2

D 1863-03 05            Specification for Mineral Aggregate Used in Built up Roofs    Table R905.9.2, Table R906.3.2,

R4402.8.12.1

D 1929-96(2001)el   Test Method for Determining Ignition Temperatures of Plastics	                          R4412.1.2

D 2126  -04              Standard Test Method for Response of Rigid Cellular Plastics to Thermal and

Humid Aging	                                                                                                R4402.12.6.5.2.17.4

D 2240—03        Test Method for Rubber Property Durometer Hardness	                                        R4410.6.4

D 2464—99        Specification for Threaded Poly (Vinly Chloride) (PVC) Plastic Pipe Fittings,

Schedule 80	                                                                             Table P2904.6, Table R4413.2.7

D 2466—02        Specification for Poly (Vinyl Chloride) (PVC) Plastic Pipe Fittings, Schedule 40	    Table P2904.6,

Table R4413.2.7

D 2467—04        Specification for Poly (Vinyl Chloride) (PVC) Plastic Pipe Fittings, Schedule 80	    Table P2904.6,

Table R4413.2.7

D 2468—96a       Specification for Acrylonitrile Butadiene Styrene (ABS) Plastic Pipe Fittings,

Schedule 40	                                                Table P2904.6, Table R4413.2.5, Table R4413.2.7

D 2565—99        Practice for Xeon Arc Exposure of Plastics Intended for Outdoor Applications	            R4412.1.2

D 2609—02         Specification for Plastic Insert Fittings for Polyethylene (PE) Plastic Pipe                Table P2904.6,

Table R4413.2.7

D 2626—04       Specification for Asphalt saturated and Coated Organic Felt Base Sheet Used

in Roofing	                                                                     R905.3.3, Table R905.9.2, R4402.7.4

D 2661—02    Specification for Acrylonitrile Butadiene Styrene (ABS) Schedule 40 Plastic Drain,     Table P3002.1,

06        Waste, and Vent Pipe and Fittings Table P3002.2, Table R4413.2.2, Table R4413.2.3, Table R4413.2.4

D 2665—04ae01 Specification for Poly (Vinyl Chloride) (PVC) Plastic Drain, Waste, and                  Table P3002.1,

07          Vent Pipe and Fittings	     Table P3002.2, Table R4413.2.2, Table R4413.2.3, Table R4413.2.4

D 2677-71(1976)  Method of Test lightability of Barbecue Briquettes (withdrawn no replacement,

1985)	                                                                                                                  Table R4413.2.4.3

D 2729—96a        Specification for Poly (Vinly Cloride)(PVC) Sewer Pipe and Fittings	                Table R4413.2.5

D 2751—96a  05  Specification for Acrylonitrile Butadiene Styrene (ABS) Sewer Pipe and Fittings   Table P3002.2,

Table R4413.2.4

D 2797-85(1999)    Standard Practice for Preparing Coal Sampler for Microscopical Analysis by

Reflected Light	                                                                                                      Table R4413.2.4

D 2842                    Standard Test Method for Water Absorption of Rigid Cellular Plastics          R4402.12.6.5.2.17.6

D 2843—99       Test Method for Density of Smoke from the Burning or Decomposition of Plastics Table R4413.1.2

D 2856                       Standard Test Method for Open Cell Content of Rigid Cellular Plastics by

the Air Pycnometer	                                                                                  R4402.12.6.5.2.17.5

D 2898-94(1999)     Test Methods for Accelerated Weathering of Fire retardant treated Wood

04                  for Fire Testing	 R802.1.4.1, R802.1.4.3, R902.2, R4409.1.4.4, R4409.14.4, R4409.16.1

D 2922                     Standard Test Method for Density of Soil and Soil Aggregate In Place by

Nuclear Methods (Shadow Depth)	                                                                  R4404.4.3.2

D 2949—01ae01      Specification for 3.25 in. Outside Diameter Poly (Vinyl Chloride) (PVC) Plastic Table P3002.1,

Drain, Waste, and Vent Pipe and Fittings                                             Table P3002.2, R4402.5.1,

Table R4413.2.2, Table R4413.2.3

D 3018                     Specification for Class A Asphalt Shingle Surfaced with Mineral Oravies	    R4402.12.6.5.1

D 3034—04 06        Specification for Type PSM Poly (Vinyl Chloride) (PVC) Sewer Pipe and Fittings

Table P3002.2, R4413.2.4

D 3201-94(2003)   Test Method for Hygroscopic Properties of Fire retardant Wood and Wood base

07                   Products 	                                                                     R802.1.4.4, R4409.1.4.4, R4409.14.5

D 3441                    Static Cone Soundings	                                                                                             R4404.18.3.3

D 3462-04 07    Specification for Asphalt Shingles Made From Glass Felt and Surfaced

with Mineral Granules	                                                                         R905.2.4, R4402.12.6.5.1

D 3498-03           Specification for Adhesives for Field Gluing Plywood to Lumber Framing

for Floor Systems	                                                                                        R4409.1.4.4, R4409.9.1.5

D 3679-05   06a Specification for Rigid Poly (Vinyl Chloride) (PVC) Siding        Table R703.4, R703.11, R703.11.1

D 3746-85(1996)e1 Test Methods for Impact Resistance of Bitumanous Roofing Systems	                       R4402.4.2.4

D 3787-01           Test Method for Bursting Strength of Textiles Constant Rate of Traverse (CRT)

Ball Burst Test	                                                                                                         R4101.17.1.15

D 4272—99         Test Method for Total Energy Impact of Plastic Films by Dart Drop	                       R4402.4.2.4

D 4402          Viscosity Determinations of Unfilled Asphalt Using the Brookfield Thermostat Apparatus  4402.8.2.3

D 5034—95           Test Method for Breaking Strength and Elongation of Textile Fabrics (Grab Test) Specifications

for Adhesives for Field Gluing Plywood to Lumber Framing for Floor Systems     R4101.17.1.15

D 6083—97a         Specification for Liquid Applied Acrylic Coating Used in Roofing 	                 Table R905.9.2,

05e01                                                                                    Table R905.11.2, Table R905.15.2, R4402.12.6.2

D 6380—01e01  03         Specification for Asphalt Roll Roofing (Organic Felt)	                       R905.2.8.2, R905.3.3

ASTM D 6509-00 Specification for Atactic Polypropylene (APP) Modified Bituminous Base Sheet Materials Using Glass Fiber Reinforcements ……………………….Table R905.11.2

D6757-05  07         Standard Specification for Underlayment Felt Containing Inorganic Fibers

Used in Steep-Slope Roofing                                                             R905.2.2, R905.2.3, R905.2.7

D7158-05  07         Standard Test Method for Wind Resistance of Sealed Asphalt Shingles (Uplift

Force/Uplift Resistance Method)                                                        R905.2.6.1, Table R905.2.6.1

E 84-06a 07   Test Method for Surface Burning Characteristics of Building Materials	N1110.AB.3.0.7

R202, R314.3, R314.5.8, R314.5.10, R315.3, R315.4, R316.1, R316.2, R802.1.4, M1601.16, M1601.3.7

R4409.1.4.4, R4409.14.1,  R4412.1.2, R4412.1.3.1.1, R4412.1.3.1.4, R4412.1.3.2.4.5,

E 96—00e01         Test Method for Water Vapor Transmission of Materials 	           M1411.4, M1601.3.4, R202,

/E96M-05                                                                                      R804.4, R4402.12.6.5.2.17.7, R4409.13.3.2.5

E 108—04        Test Methods for Fire Tests of Roof Coverings                      R902.1, R902.2, R4402.2.1, R4402.5.1,

07a                                                                                                                              R4402.12.1.2, R4409.16.1

E 119-00a Test Methods for Fire Tests of Building Construction and Materials  R314.1.2, R314.4, R317.1, R317.3.1

07                                                                                                                                       R4412.1.2, R4412.1.3.2

E 136—99e04  04   Test Method for Behavior of Materials in a Vertical Tube Furnace at 750 Degree C       R202

E 152—95        Methods of Fire Tests of Door Assemblies	                                                  R314.3, R4412.1.3.1.4

E 163                Methods of Fire Tests for Window Assemblies (Withdrawn)	                                R4407.4.2.12.8

E 283-04 Standard Test Method for Determining the Rate of Air Leakage through Exterior Windows, Curtain Walls and Doors Under Specified Pressure Differences Across the Specimen R806.4, N1106.AB.1.1, N1106.AB.2.4, R4409.13.3.2.5, Appendix G B3.4

E 330-02          Test Method for Structural Performance of Exterior Windows, Curtain Walls, and

Doors by Uniform Static Air Pressure Difference 	   R613.3, R613.4.1, R4410.6.4, R4410.6.6.1

E 331—00        Test Method for Water Penetration of Exterior Windows, Skylights, Doors and

Curtain Walls by Uniform Static Air Pressure Difference                                       R613.4, R4410.6.4

E 903-96 		Test Method for Solar Absorptance, Reflectance, and Transmittance

of Materials Using Integrating Spheres		   N1104.A.4, Appendix G C4.2.1.5

E 1300—04e01 or 98 (HVHZ) Practice for Determining Load Resistance of Glass in Buildings  . . . . . . . . . . . . . . . . . . . R613.3.1, R4410.2.2

E 1886—02 or 05       Test Method for Performance of Exterior Windows, Curtain Walls, Doors and Storm

06               Shutters Impacted by Missiles and Exposed to Cyclic Pressure Differentials             R301.2.1.2

E 1918-06	Standard Test Method for Measuring Solar Reflectance of Horizontal

And Low-Sloped Surfaces in the Field			N1104.A.4

E 1996—02 or 05       Specification for Performance of Exterior Windows, Curtain Walls, Doors and Storm

06              Shutters Impacted by Windborne Debris in Hurricanes	                                       R301.2.1.2

E 2112-07Standard Practice for Installation of Exterior Windows, Doors, and Skylights R613.7.5

F 405—97 05         Specifications for Corrugated Polyethylene (PE) Tubing and Fittings	                Table R4413.2.5

F 409—02         Specification for Thermoplastic Accessible and Replaceable Plastic Tube and

Tubular Fittings	                                                              Table P2701.1, P2702.3, Table R4413.2.7

F 437—99  06        Specification for Threaded Chlorinated Poly (Vinyl Chloride) (CPVC) Plastic

Pipe Fittings, Schedule 80	                                                               Table P2904.6, Table R4413.2.7

F 438—04          Specification for Socket type Chlorinated Poly (Vinyl Chloride) (CPVC) Plastic

Pipe Fittings, Schedule 40	                                                               Table P2904.6, Table R4413.2.7

F 439—02e01 06         Specification for Socket type Chlorinated Poly (Vinyl Chloride) (CPVC) Plastic

Pipe Fittings, Schedule 80	                                                               Table P2904.6, Table R4413.2.7

F 628—01 06e01  Specification for Acrylonitrile Butadiene Styrene (ABS) Schedule 40 Plastic Waste  and Vent Pipe with a Cellular Core Table P3002.1,  Table P3002.2, Table R4413.2.2, Table R4413.2.3, Table R4413.2.4

F 891—00e01        Specification for Coextruded Poly (Vinyl Chloride) (PVC) Plastic Pipe with a       Table P3002.1,

04         Cellular Core  Table P3002.2, Table R4413.2.2, Table R4413.2.3, Table R4413.2.4, Table R4413.2.5

F 1346-91(1996)  Performance Specification for Safety Covers and Labeling Requirements for

(2003)                Swimming Pools, Spas and Hot Tubs	                                                                             R202

F 1554—99 04e01Standard Specifications for Anchor Bolts Steel 36, 55 and 105 ksi Yield Strength     Table R4413.2.5

G 26—77            Practice for Operating Light Exposure Apparatus (Xenon Arc Type) With and

Without Water for Exposure of Nonmetallic Materials (Withdrawn)	                          R4412.1.2

G 53—96            Practice for Operating Light and Water Exposure Apparatus (Fluorescent UV

condensation type) for Exposure of Nonmetallic Materials	                                 R4401.17.1.15

G 60                     Standard Practice for Conducting Cyclic Humidity Exposures	                             R4409.6.17.2.2.8

G 85                     Standard Practice for Modified Salt Spray (Fog) Testing	                                        R4402.6.5

AWPA           American Wood Preservers’ Association

801 Alabama Avenue 2nd Floor,

Selma, AL 36702-0388

Standard                                                                                                              Referenced in code

reference number    Title                                                                                           section number

C2—01            Lumber, Timbers, Bridge Ties and Mine Ties — Preservative Treatment

by Pressure Processes 	                                      R319.1, R323.1.7, Table R905.8.5, R4409.1.4.5

C3—99            Piles — Preservative Treatment by Pressure Processes	R319.1, R323.1.7, R4404.7.1.3, R4409.1.4.5

C4—99            Poles — Preservative Treatment by Pressure Processes	                     R319.1, R323.1.7, R4409.1.4.5

C5—03            Posts—Pressure Treatment by Pressure Processes	                                                    R4409.1.4.5

C6—99            Crossties and Switch Ties Preservative Treatment by Pressure Processes	  R4409.1.4.5, R4409.21.9

C7—96            Western Red Cedar, Northern White Cedar & Alaska yellow Cedar Poles Preservative

Treatment of Incised Pole Butts by the Thermal process (Withdrawn)	                       R4409.1.4.5

C8—96            Western Red & Alaska Yellow Cedar Poles Preservative Treatment by the Full

Length Thermal process (Withdrawn)	                                                                                 R4409.1.4.5

C9—03            Plywood — Preservative Treatment by Pressure Processes	       R319.1, R323.1.7, R4409.1.4.5

C10—96          Lodgepole Pine Poles Preservative Treatment by the Full Length Thermal Process	         R4409.1.4.5

C11—01          Wood Blocks for Floors & Platforms Pressure Treatment by the Pressure Process	         R4409.1.4.5

C14—03          Wood for Highway Construction Pressure Treatment by the Pressure Process	         R4409.1.4.5

C16—03          Wood used on Farms Pressure Treatment	                                                                  R4409.1.4.5

C18—99          Standard for Pressure Treated Material in Marine Construction	       R319.1, R323.1.7, R4409.1.4.5

C20—99          Structural Lumber—Fire retardant Treatment by Pressure Processes 	                       R4409.1.4.5

C22—96          Lumber and Plywood for Permanent Wood Foundations— Preservative Treatment

by Pressure Processes	                                  R319.1, R323.1.7, R402.1.2, R504.3, R4409.1.4.5

C23—03          Round Poles and Posts Used in Building Construction— Preservative Treatment

by Pressure Processes 	                                                                   R319.1, 323.1.7, R4409.1.4.5

C25—03           Sawn Crossarms Pressure Treatment	                                                                                 R4409.1.4.5

C26—57           Crossarms Non Pressure Treatment	                                                                                 R4409.1.4.5

C28—99           Standard for Preservative Treatment by Pressure Process of Structural Glued

Laminated Members and Laminations Before Gluing 	                                                    R4409.1.4.5

C29—01          Lumber to be used for the Harvesting Storage and Transportation of Food Stuffs

Preservative Treatment by Pressure Processes	                                                                  R4409.1.4.5

M1—01           Standard for the Purchase of Treated Wood Products	                                                    R4404.7.1.4

M2—01            Standard for the Inspection of Wood Products Treated with Preservatives	                       R4404.7.1.4

M4—02            Standard for the Care of Preservative treated Wood Products                      R4404.7.1.4, R4409.1.4.5

AWS                American Welding Society

550 NW Le Jeune Road

Miami, FL 33126

Standard                                                                                                              Referenced in code

reference number    Title                                                                                           section number

B2.1               Standard Welding Procedure and Performance Qualification	                                        R4408.1.3

C5.4               Recommended Welding Practice for Stud Welding	                                                       R4408.1.3

D1.1               Structural Welding Code Steel	                                                                                                  R4408.1.3

D1.2               Structural Welding Code Aluminum	                                                                                    R4406.1.3

D1.3               Structural Welding Code Sheet Metal	                                                                                    R4408.1.3

D1.4               Structural Welding Code Reinforcing Steel	       R4405.4.4, R4405.8.4.8, R4407.2.1.1, R4408.1.3

D9.1               Specification for Welding of Sheet Metal	                                                                     R4408.1.3

D10.9             Standard for Qualification of Welding Procedures and Welders for Piping and Tubing          R4408.1.3

AWWA         American Water Works Association

6666 West Quincy Avenue

Denver, CO 80235

Standard                                                                                                              Referenced in code

reference number    Title                                                                                           section number

C110—98               Standard for Ductile iron and Gray iron Fittings, 3 Inches through 48

Inches, for Water 	                                                               Table P2904.6, Table R4413.2.7

C511—00               Reduced Pressure Principle Backflow Prevention Assembly 	               Table P2902.2, P2902.2.5,

P2902, P2902.4.1

CGSB          Canadian General Standards Board

11 Laurier Street, Place du Portage III, 6B1

Gatineau, Quebec, Canada K1A 1G6

Standard                                                                                                              Referenced in code

reference number    Title                                                                                           section number

37–GP—52M—(1984) Roofing and Waterproofing Membrane, Sheet Applied, Elastomeric R905.12.2, R4402.4.2.4

CISPI          Cast Iron Soil Pipe Institute

Suite 419

5959 Shallowford Road

Chattanooga, TN 37421

Standard                                                                                                              Referenced in code

reference number    Title                                                                                           section number

301—04a       Specification for Hubless Cast Iron Soil Pipe and Fittings for Sanitary  Table P3002.1, Table P3002.2,

and Storm Drain, Waste and Vent Piping Applications	               Table R4413.2.2, Table R4413.2.3,

Table R4413.2.4, Table R4413.2.5

CPSC         Consumer Product Safety Commission

4330 East West Highway

Bethesda, MD 20814 4408

Standard                                                                                                              Referenced in code

reference number    Title                                                                                           section number

16 CFR Part 1201—(1977)    Safety Standard for Architectural Glazing        R308.1.1, R308.3, R4410.2.1.3,

R4410.2.3.1.2, R4410.2.4.2

CSA            Canadian Standards Association

8501 East Pleasant Valley Road

Cleveland, OH 44131 5575

Standard                                                                                                              Referenced in code

reference number    Title                                                                                           section number

A257.1—03    Nonreinforced Circular Concrete Culvert, Storm Drain, Sewer Pipe and Fittings        Table R4413.2.4

A257.2—03    Reinforced Circular Concrete Culvert, Storm Drain, Sewer Pipe and Fittings             Table R4413.2.4

B125—01      Plumbing Fittings	                                                                  Table P2902.2.2, P2902.3.1, P3003.3.5

B137.2—02   PVC Injection moulded Gasketed Fittings for Pressure Applications   Table P2904.6, Table R4413.2.7

B181.1—02        Plastic Drain and Sewer Pipe Fittings	                              Table R4413.2.2, Table R4413.2.3

B181.2—02        PVC Drain, Waste Vent Pipe Fittings	                              Table R4413.2.2, Table R4413.2.3

B181.3—02        Polyolefin Laboratory Drainage System	                              Table R4413.2.2, Table R4413.2.3

B182.2—02        PVC Sewer Pipe and Fittings (PSM Type)	                              Table R4413.2.4, Table R4413.2.5

B182.4—02        Profile PVC Sewer Pipe and Fittings	                              Table R4413.2.4, Table R4413.2.5

DASMA         Door and Access Systems Manufacturers Association International

1300 Summer Avenue

Cleveland, OH 44115-2851

Standard                                                                                                              Referenced in code

reference number    Title                                                                                           section number

ANSI/DASMA 108- 05   Standard Method for Testing Sectional Garage Doors and Rolling Doors:  Determination of Structural Performance Under Uniform Static Air Pressure Difference                                        R613.4.1, R613.4.2

ANSI/DASMA 115-05  Standard Method for Testing Garage Doors and Rolling Doors:  Determination

of Structural Performance Under Missile Impact and Cyclic Wind Pressure                    R301.2.1.2

DHS/FEMA           Department of Homeland Security

Federal Emergency Management Agency

Federal Center Plaza

500 C Street, SW

Washington, DC 20472

Standard                                                                                                              Referenced in code

reference number    Title                                                                                           section number

CFR 44           Emergency Management and Assistance

Part 59         59 Criteria for Land Management Use, General Provisions

Part 60         60 Criteria for Land Management Use, Flood Plain Management Regulation         R301.2.4, M1401.5,

P2601.3

FIA-TB-11-01

TB–2—93      Flood–resistant Materials Requirements	                                                                       R323.1.7

DOC/NIST              Department of Commerce

National Institute of Standards and Technology

100 Bureau Drive Stop 3460

Gaithersburg, MD 20899

Standard                                                                                                              Referenced in code

reference number    Title                                                                                           section number

CS 236              Mat Formed Particleboard	                                                                         R4409.1.4.6, R4409.2.1.6

PS 1—95  07        Construction and Industrial Plywood R404.2.1, Table R404.2.3, R503.2.1, R604.1, R803.2.1,

R404.21, Table R404.2.3, R503.2.1, R604.1, R803.2.1, R4409.1.4.6, R4409.2.1.2

PS 2—92  04    Performance Standard for Wood–based Structural–use Panels   R404.2.1, Table R404.2.3, R503.2.1,

R604.1, R803.2.1, R404.21, Table R404.2.3, R503.2.1, R604.1,

R803.2.1, R4409.1.4.6, R4409.2.1.2

PS 56                Structural Glued Laminated Timber	                                                                                 R4409.1.4.6

PS 20—99 05       American Softwood Lumber Standard	                    R404.2.1, R502.1.1, R602.1.1, R802.1.1,

Table R404.2.3, R503.2.1, R604.1, R803.2.1, R4409.1.4.6, R4409.2.1.8

DOE	United States Department of Energy

c/o Superintendent of Documents

U.S. Government Printing Office

Washington, DC 20402-9325

Standard reference number	Title	Referenced in Code Section Number

DOE, 10 CFR, Part 430 Subpart B, App. E-1998 Uniform Test Method for Measuring the Energy Consumption of Water Heaters Table N1108.AB.3.2F, Subpart B, App. E-1998, N1112.AB3.1.1, N1112.AB.3.2.1

DOE, 10 CFR, Part 430 Subpart B, App. M Uniform Test Method for Measuring the Energy Consumption of Central Air Conditioners                                                        N1107.AB.3.1

DOE, 10 CFR, Part 430 Subpart B, App N-1998 Uniform Test Method for Measuring the Energy Consumption of Furnaces                                                                            Table N1108.AB.3.2E

DOE, 10 CFR, Part 430	Uniform Test for Measuring the Energy Consumption of Vented

Subpart B, App O-1998	Home Heating Equipment				N1100.7.3

EPACT, 1992 42 USC 6831 Energy Policy Act of 1992 et seq. Public Law 102-486 N1107.AB.3.2

NAECA, 1987 National Appliance Energy Conservation Act of 1987 Tables N1107.AB.3.2A, N1107.AB.3.2B, N1108.AB.3.2E

DOL/OSHA       Department of Labor

Occupational Safety and Health Administration

Frances Perkins Building

200 Constitution Avenue, NW

Washington, DC 20210

Standard                                                                                                              Referenced in code

reference number    Title                                                                                           section number

29 CFR 1910              General Industry Occupational Health & Safety Standards	                                        R4403.7.3

29 CFR 1926 650(P) Excavation Safety Act	                                                                                                  R4404.1.1

DOT        Department of Transportation

400 Seventh St. S.W.

Washington, DC 20590

Standard                                                                                                              Referenced in code

reference number               Title                                                                                section number

14 CFR Part 150 (2005)    Airport Noise Compatibility Planning, Federal Aviation Administration	                    R325

FCPA      Florida Concrete & Products Association, Inc.

3030 Dade Avenue

Orlando, Florida 32804

Standard                                                                                                              Referenced in code

reference number               Title                                                                                                                section number

FCPA—97                   Guide to Concrete Masonry Residential Construction in High Wind Areas	           R301.2.1.1

Florida Codes     Florida Building Commission

c/o Florida Department of Community Affairs

Building Codes and Standards

2555 Shumard Oak Boulevard

Tallahassee, FL 32399-2100

RAS 111                                                                                   Add:                                                                     R903.3

TAS 107…………………………                                            Add:   …………………..R905.6.2.1, Table R905.6.2.1

TAS 202                                                                                    Add:                                                 R613.3.1, R613.4.2

FM                Factory Mutual Global Research

Standards Laboratories Department

1151 Boston Providence Turnpike

Norwood, MA 02062

Standard                                                                                                              Referenced in code

reference number    Title                                                                                           section number

4450—(1989)        Approval Standard for Class 1 Insulated Steel Deck Roofs—with Supplements

through July 1992	                                                                           R906.1, R4412.1.3.2.5.2

4470 (1992)            Approval Standard for Class 1 Roof Covers                         R4402.2.1, R4402.4.1.1, R4402.4.2.4

4880—(20015)        American National Standard for Evaluating Insulated Wall or Wall and

Roof/Ceiling Assemblies, Plastic Interior Finish Materials, Plastic Exterior

Building Panels, Wall/Ceiling Coating Systems, Interior or Exterior

Finish Systems	                                                                               R314.4, R314.6, R4412.1.3.1.4

FRSA           Florida Roofing, Sheet Metal and Air-Conditioning Contractors Association, Inc.

411 Metric Avenue

Winter Park, Florida 32793

FRSA/TRI 07320/8-05                                                             Add:                                 R905.3, R905.3.3, R905.3.7.1

FS                 Federal Specification

941 Jefferson Davis Highway, Suite 104

Arlington, VA 22202

TT P 1536A (1975) Federal Specification for Plumbing Fixture Setting Compound	P3003.4.5

TTC 555B Test Specification for Wind Driven Rain Infiltration Resistance	 	R4402.12.6.3.1

FSEC

Florida Solar Energy Center

1679 Clearlake Road

Cocoa, FL 32922-5703

Standard reference	Title							Referenced in Code

number										Section Number

FSEC-RR-54-00		"The HERS Rating Method and the Derivation of the

Normalized Modified Loads Method", October 11, 2000,	N1113.A.2.1

Fairey, P., J. Tait, D. Goldstein, D. Tracey, M. Holtz, and							R. Judkoff.   Available online at:

http://www2.fsec.ucf.edu/en/publications/html/FSEC-RR-54-00/index.htm

2010			EnergyGauge USA Fla/Res computer program	N1100.2.2, N1100.3, N1100.3.2,

N1100.A.1, N1100.A.2, N1101.A,

N1101.A.3, N1102.A.1, N1104.A.1,

N1104.A.3, N1104.A.4, N1107.A.1,

N1108.A.1, N1110.A.1, N1110.A.2,

N1110.A.3, N1112.A.1, N1113.A.2.1

FTC	U.S. Federal Trade Commission

Sixth Street and Pennsylvania Avenue, N.W.

Washington, DC 20580

Standard reference number	Title				Referenced in Code Section Number

FTC, 16 CFR, Part 460,		FTC Labeling and Advertising of Home Insulation

Amended Effective 4/29/96			`			      N1100.7, Appendix G B1.2

FWC           Florida Wood Council

P.O. Drawer 1076

Mount Dora, Florida 32757-1076

1997 		Guide to Wood Construction in High Wind Areas				R301.2.1.1

GA               Gypsum Association

810 First Street, Northeast, Suite 510

Washington, DC 20002-4268

GA 253-99  07                                                                                                                              Table R602.2(1)

GAMA	Gas Appliance Manufacturers Association

PO Box 9245

Arlington, VA 22209

Standard reference number	Title				Referenced in Code Section Number

GAMA Consumer's Directory of Certified Efficiency Ratings for Water Heating Equipment Table N1112.AB.3.5, Appendix G C4.3.1.3

HI	Hydronics  Institute

P.O. Box 218

Berkeley Heights, NH  07922

Standard reference number	Title				Referenced in Code Section Number

H.I., HBS 86-1989 Testing and Rating Standard for Heating Boilers Tables N1108.AB.3.2F

HUD	U.S. Dept. Housing and Urban Development

451 7th Street S.W.

Washington, DC 20410

Standard reference number	Title				Referenced in Code Section Number

HUD, 24 CFR 3282-3283	Manufactured Home Procedural and Enforcement Regulations		N1100.7

HUD, 42 CFR 70, s. 5401	Manufactured Home Construction and Safety Standards

(24 CFR 3280)										N1100.7

HUD, 42 USC 77, s. 6295	 Energy Conservation Standards					N1100.7

ICC       International Code Council

900 Montclair Road

Birmingham, Alabama 35213-1206

Standard                                                                                                              Referenced in code

reference number    Title                                                                                           section number

IBHS-2005                   Guideline for Hurricane Resistant Residential Construction 2005

with errata for the first printing                                                                                 R301.2.1.1

ISO	International Standards Organization

1, rue de Varembe, Case postale 56,

CH-1211 Geneve 20, Switzerland

Standard reference number	Title				Referenced in Code Section Number

ISO 9806 (1994, 1995) Test Methods for Solar Collectors

Part 1: December 1, 1994 Thermal Performance of glazed liquid heating collectors including pressure drop

Part 2: Qualification test procedures, August 15, 1995.

Part 3: Thermal performance of unglazed liquid heating collectors (sensible heat transfer only) including pressure drop, December 15, 1995.                                                      N1112.AB.3.4

ISO 13256-1 (1998) Part 1 Water-Source Heat Pumps-Testing and Rating for Performance-

Water-to-Air and Brine-to-Air Heat Pumps                                           Table N1107.AB.3.2B

NAAMM      National Association of Architectural Metal Manufacturers

8 South Michigan Avenue

Chicago, IL 60603

Standard                                                                                                              Referenced in code

reference number    Title                                                                                           section number

ANSI/NAAMM MBG 5XX   Metal Grating Manual	                                                                                    R4408.1.3

NAIMA        North American Insulation Manufacturer’s Association

44 Canal Center Plaza, Suite 310

Alexandria, VA 22314

Standard                                                                                                              Referenced in code

reference number    Title                                                                                           section number

NAIMA 2002 Fibrous Glass Duct Construction Standards, Fifth Edition N1110.AB.3.2

NAIMA 2002 Fibrous Glass Duct Liner Standard, Third edition N1110.AB.2.4, N1110.AB.3

AH 116 06—02      Fibrous Glass Duct Construction Standards	                                  M1601.6, M1601.6.2.3

NFPA         National Fire Protection Association

1 Batterymarch Park

Quincy, MA 02269

Standard                                                                                                              Referenced in code

reference number    Title                                                                                           section number

70—05 08           National Electrical Code (NEC)	                                                                                       E3301.1

70A—05         National Electric Code (NEC) for One and Two Family Dwellings	             E3301.1, G2402.3

101—03          Life Safety Code	                                                                                                                     R324.1

259—03 Test Method for Potential Heat of Building Materials. . . . . 2603.4.1.10, 2603.5.3, 2612.3.2.4.4, R314.5.7, R4412.1.3.2.4.4

286—06          Standard Methods of Fire Tests for Evaluating Contribution of Wall and

Ceiling Interior Finish to Room Fire Growth	                      R314.4, R314.6, R315.4, R4412.1.3.1.4

501—05  Standard on Manufactured Housing   . . . . . . . . . . . . . . . . . . .R202

  - Standard for the Installation of Carbon Monoxide (CO)

Warning Equipment in Dwelling Units     			                R313

NFRC	National Fenestration Rating Council, Inc.

8484 Georgia Avenue, Suite 320

Silver Spring, MD 20910

Standard reference number	Title	Referenced in Code Section Number

NFRC 100-04	Procedure for Determining Fenestration Product U-factors	N1100.6.5, Appendix G B2.1.1

NFRC 200-04	Procedure for Determining Fenestration Product Solar Heat Gain Coefficients

and Visible Transmitttance at Normal Incidence	N1100.6.5, Appendix G B2.1.1, C2.1.4,

NRCA           National Roofing Contractors Association

10255 W. Higgins Road, Suite 600

Rosemont, IL 60018

Standard                                                                                  	            Referenced in code

reference number    Title                                                                                           section number

P 0405            Roofing and Waterproofing Manual, 5th Edition	                                                       R4402.2.1

NSF               National Sanitation Foundation

3475 Plymouth Road

Ann Arbor, MI 48105

RMI/SMA     Rack Manufacturer’s Institute/Storage Equipment Manufacturer’s Association

(A member of the Material Handling Industry of America)

8720 Red Oak Blvd., Suite 201

Charlotte, NC 28217

RP1—90	Minimum Requirements for Non Reinforced Black EPDM Rubber Sheets	R905.12.2

RP2—90	Minimum Requirements for Fabric Reinforced Black EPDM Rubber Sheets	R905.12.2

RP3—85    Minimum Requirements for Fabric Reinforced Black Polychloroprene Rubber Sheets	R905.12.2

RCSC           Research Council on Structural Connections

c/o Stanley D. Lindsey & Associates Ltd.

224 Metro Center Blvd., Suite 208

Nashville, TN 37228-1320

RCSC	Load and Resistance Factor Design Specification for Structural Joints Using A325 and A490 Bolts, 1988	R4408.1.3

SDI             Steel Door Institute

P.O. Box 25

Fox River Grove, IL 60021

MOC1	SDI Manual of Construction with Steel Deck			R4408.1.3

DDP	Deck Damage and Penetrations					R4408.1.3

DDM02	Diaphragm Design Manual				R4408.1.3, R4408.9.4

SDI, LRFD	Design Manual for Composite Beams and Girders with Steel Deck	R4408.1.3

SPD2	Standard Practice Details						R4408.1.3

NO. 30	Steel Deck Institute Design Manual					R4408.1.3

SDI           Steel Door Institute

c/o Wherry Associates

30200 Detroit Road

Cleveland, Ohio 44145 1967

ANSI A250.13—03	Testing and Rating of Severe Windstorm Resistant Components for Swinging Door Assemblies	R613.4.4.1

SJI             Steel Joist Institute

3127 10th Avenue, North

Myrtle Beach, SC 29577-6760

SJI	Standard Specifications, Load Tables and Weight Tables for Steel Joists and Joist Girders	     R4408.1.3

SJI	Structural Design of Steel Joist Roofs to Resist Ponding Loads, Technical Digest No. 3	R4408.1.3

SJI	Structural Design of Steel Joist Roofs to Resist Uplift Loads, Technical Digest No. 9	R4408.1.3

SJI	Vibration of Steel Joist Concrete Slab Floors, Technical Digest No. 5	R4408.1.3

SJI	Welding of Open Web Steel, Technical Digest No. 8			R4408.1.3

SJI	60 Year Steel Joist Manual					R4408.1.3

SMACNA   Sheet Metal & Air Conditioning Contractors National Assoc., Inc.

4021 Lafayette Center Drive

Chantilly, VA 22021

Standard                                                                                                              Referenced in code

reference number    Title                                                                                           section number

SMACNA—85       HVAC Air Duct Leakage Test Manual	                     M1601.5.3, N1110.AB.3.1.3

SMACNA—95       HVAC Duct Construction Standards–Metal and Flexible	                                          M1601.5

SRCC	Solar Rating and Certification Corporation

c/o Florida Solar Energy Center

1679 Clearlake Road

Cocoa, FL 32922-5703

Standard reference number	Title	Referenced in Code Section Number

FSEC		Directory of Certified Solar Systems					N1112.AB.3.4

SRCC TM-1	Solar Domestic Hot Water System and Component Test Protocol,

December 6, 2002							N1112.AB.3.4

SSPC         Society for Protective Coatings

40 24th Street, 6th Floor

Pittsburgh, PA 15222-4656

SSPC Paint 15	Steel Joist Shop Paint							R4408.1.3

SSPC/AISC	Guide to the Shop Painting of Structural Steel				R4408.1.3

SPRI           Single-Ply Roofing Institute

77 Rumford Avenue, Suite 3-B

Waltham, MA 02453

Standard                                                                                                              Referenced in code

reference number    Title                                                                                          section number

ES 1-98        Wind Design Standard for Edge Systems Used with Low Slope Roofing Systems                        R903.3

STI              Steel Tube Institute of North America (Welded Steel Tube Institute, Inc.)

2000 Ponce de Leon, Suite 600

Coral Gables, Florida 33134

WSTI/STI	Manual of Cold Formed Structural Steel Tube				R4408.1.3

TECO          Timber Company Inc.

2402 Daniels Street

Madison, WI 53704

PRP 133	Performance Standards and Policies for Structural Use Panels		R4409.1.4.8, R4409.2.1.2

TPI        Truss Plate Institute

218 N. Lee Street, Suite 312

Alexandria, VA 22314

Standard                                                                                                              Referenced in code

reference number    Title                                                                                           section number

BCSI  06    Guide to Good Practice for Handling, Installing Restraining & Bracing of Metal Plate           R502.1.3.2, 802.1.6.3,

WTCA           Connected Wood Trusses                                            R4409.1.4.9, R4409.6.17.2.4.1, R4409.6.17.2.4.3

TPI 1—02      National Design Standard for Metal plate connected Wood Truss Construction                   R502.1.3.1,

R502.1.3.2, R802.1.6.2, R802.2.9.1, R4409.1.4.9, R4409.6.17.2.1.1, R4409.6.17.2.2.8

UL           Underwriters Laboratories, Inc.

333 Pfingsten Road

Northbrook, IL 60062

Standard                                                                                                              Referenced in code

reference number    Title                                                                                           section number

9—00           Standard for Fire Tests of Window Assemblies	                                                             R4407.4.2.12.8

181-05 Standard for Factory-made Air Ducts and Air Connectors N1110.AB.3.0.7, N1110.AB.3.7.1

181A-05 Closure Systems for Use with Rigid Air Ducts and Air Connectors M1601.2, M1601.3.1, M1601.6.2.3, M1601.6.4.2, M1601.6.4.5, M1601.10.1, N1110.AB.3.0.7

181B-05 Closure Systems for Use with Flexible Air Ducts and Air Connectors N1110.AB.3.0.7

536—97      Flexible Metallic Hose—with Revisions through October 2000	                                           M2202.3

580—94      Test for Uplift Resistance of Roof Assemblies	                                                R4408.1.3, R4408.9.4.6

723-03 Standard for Test for Surface Burning Characteristics of Building Materials M1601.1.3.7, N1110.AB.3.0.7

727-06 Standard for Oil-Fired Central Furnaces, with Revisions through January 1999 Table N1108.AB.3.2E

731-95 Standard for Oil-Fired Unit Heaters, with revisions through January 1999 Table N1108.AB.3.2E

790—04      Tests for Fire Resistance of Roof Covering Materials— with Revisions through July 1998   R902.1,

R4402.2.1, R4402.5.1, R4409.1.4.10, R4402.12.1.2

795—01     Commercial Industrial Gas Heating Equipment	                                                        G2442.1, G2452.1

834—04     Heating, Water Supply, and Power Electric—with Revisions through November 1998	           M2001.1.1

1040—96      Fire Test of Insulated Wall Construction—with Revisions through June 2001               R314.4, R314.6,

R4412.1.3.1.4

1482—98       Solid fuel Type Room Heaters—with Revisions through January 2000	                            M1410.1

1715—97       Fire Test of Interior Finish Material	                                                  R314.4, R314.6, R4412.1.3.1.4

1777—04      Chimney Liners—with Revisions through July 1998                          R1001.8.1, R1001.15, M1801.3.4,

G2425.12, G2425.15.4

2017—00       Standard for the General Purpose Signaling Devices and Systems	                                   R4101.17.1.9

ANSI/UL 2034 - 96, Standard for Single and Multiple Station CO Alarms……R202

UL 2075 - 04, Gas and Vapor Detector Sensor………R202

2158—97       Standard for Electric Clothes Dryer with Revisions through February 1999	                            M1501.1

WDMA      Window & Door Manufacturers Association

1400 East Touhy Avenue, #470

Des Plaines, IL 60018

Standard                                                                                                              Referenced in code

reference number    Title                                                                                           section number

101/I.S. 2—97   Voluntary Specifications for Aluminum, Vinyl (PVC) and Wood Windows and Glass Doors R613.3

101/I.S.2/NAFS-02 Voluntary Performance Specifications for Windows, Doors and Unit Skylights R308.6.9, R613.3, N1106.AB.1.1

101/IS2/A440-05

WPPC       Wood Products Promotional Council

c/o Florida Wood Council

1300 Limit Avenue

Mount Dora, FL 32758

WQA         Water Quality Association

4151 Naperville Road

Lisle, IL 60532

Chapter 44:   Referenced Standards.  Revise to read as follows:

High Velocity Hurricane Zone.  Add Chapter 44 from the 2009 Florida Building Code, Residential to read as shown.

Chapter 44:  High Velocity Hurricane Zone

Appendix D (IFGS):  Recommended Procedure for Safety Inspection of An Existing Appliance Installation.  Change to read as shown.

Appendix D (IFGS):  Recommended Procedure for Safety Inspection of An Existing Appliance Installation.  Reserved.

Appendix E:  Chapter 9b-53, Standard for Mitigation of Radon in Existing Buildings.  Change to read as shown. (See 2004 FBC)

Appendix E:  Chapter 9b-53, Standard for Mitigation of Radon in Existing Buildings.

Appendix F:  Chapter 9b-52, Florida Standard for Passive Radon-Resistant New Residential Building Construction.  Change to read as shown. (See 2004 FBC)

Appendix F:  Chapter 9b-52, Florida Standard for Passive Radon-Resistant New Residential Building Construction.

Appendix G Swimming Pools, Spas and Hot Tubs.  Change to read as shown.

APPENDIX G

SUPPLEMENTAL INFORMATION FOR CHAPTER 11

[Add from ’07 FBC-B Appendix 13-A]

Appendix H Patio Covers.  Change to read as shown.

Appendix H Patio Covers.  Reserved.

Appendix I Private Sewage Disposal.  Change to read as shown.

Appendix I Private Sewage Disposal.  Reserved.

Appendix J Existing Buildings and Structures.  Change to read as shown.

Appendix J Existing Buildings and Structures.  Reserved.

Appendix K Sound Transmission.  Change to read as shown.

Appendix K Sound Transmission.  Reserved.

Appendix L Permit Fees.  Change to read as shown.

Appendix L Permit Fees.  Reserved.

Appendix M Home Day Care – R-3 Occupancy.  Change to read as shown.

Appendix M Home Day Care – R-3 Occupancy.  Reserved.

Appendix N Venting Methods.  Change to read as shown.

Appendix N Venting Methods.  Reserved.

Appendix O Gray Water Recycling Systems.  Change to read as shown.

Appendix O Gray Water Recycling Systems. Reserved.

Appendix O

APPENDIX O

GRAY WATER RECYCLING SYSTEMS

Note: Section P2601.2 of the Florida Building Code, Residential requires all plumbing fixtures that receive water or waste to discharge to the sanitary drainage system of the structure. To allow for the use of a gray water recycling system, Section P2601.2 of the Florida Building Code, Residential should be revised to read as follows:

P2601.2 Connections. Plumbing fixtures, drains and appliances used to receive or discharge liquid wastes or sewage shall be directly connected to the sanitary drainage system of the building or premises, in accordance with the requirements of this code. This section shall not be construed to prevent indirect waste systems.

Exception: Bathtubs, showers, lavatories, clothes washers and laundry trays are not required to discharge to the sanitary drainage system where those fixtures discharge to an approved gray water recycling system.  Any sewage that discharges from the building must be connected to a sanitary drainage system of the building or premises.  The sanitary drainage system shall discharge either to public sewer or to an onsite sewage treatment and disposal system in accordance with the State of Florida Standards for Onsite Sewage Treatment and Disposal Systems, Chapter 64E-6, Florida Administrative Code.

SECTION AO101 GENERAL

Section AO101.1 Scope, revise text to read as follows:

AO101.1 Scope. The provisions of this appendix shall govern the materials, design, construction and installation of gray water systems for flushing of water closets and urinals (see Figure AO101.1(1)).

Section AO101.2 Definition, revise text to read as follows:

AO101.2 Definition. The following term shall have the meaning shown herein.

GRAYWATER. As defined by 381.0065(2)(b) and (d) Florida Statutes, “Graywater” means that part of domestic sewage that is not blackwater, including waste from the bath, lavatory, laundry, and sink, except kitchen sink waste.  “Blackwater” means that part of domestic sewage carried off by toilets, urinals, and kitchen drains

AO101.3 Permits. Permits shall be required in accordance with Section R105 of the Florida Building Code, Residential.

Section AO101.4 Installation, revise text to read as follows:

AO101.4 Installation. In addition to the provisions of Section AO101, systems for flushing of water closets and urinals shall comply with Section AO102. Except as provided for in Appendix O, all systems shall comply with the provisions of the Florida Building Code, Residential.

AO101.5 Materials. Above-ground drain, waste and vent piping for gray water systems shall conform to one of the standards listed in P3002.1(1) of the Florida Building Code, Residential. Gray water underground building drainage and vent pipe shall conform to one of the standards listed in P3002.1(2) of the International Residential Code.

AO101.6 Tests. Drain, waste and vent piping for gray water systems shall be tested in accordance with Section P2503 of the Florida Building Code, Residential.

AO101.7 Inspections. Gray water systems shall be inspected in accordance with Section P2503 of the Florida Building Code, Residential.

AO101.8 Potable water connections. Only connections in accordance with Section AO102.3 shall be made between a gray water recycling system and a potable water system.

AO101.9 Waste water connections. Gray water recycling systems shall receive only the waste discharge of bathtubs, showers, lavatories, clothes washers or laundry trays.

AO101.10 Filtration. Gray water entering the reservoir shall pass through an approved filter such as a media, sand or diatomaceous earth filter.

AO101.10.1 Required valve. A full-open valve shall be installed downstream of the last fixture connection to the gray water discharge pipe before entering the required filter.

AO101.11 Collection reservoir. Gray water shall be collected in an approved reservoir constructed of durable, nonabsorbent and corrosion-resistant materials. The reservoir shall be a closed and gas-tight vessel. Access openings shall be provided to allow inspection and cleaning of the reservoir interior.

AO101.12 Overflow. The collection reservoir shall be equipped with an overflow pipe having the same or larger diameter as the influent pipe for the gray water. The overflow pipe shall be indirectly connected to the sanitary drainage system.

AO101.13 Drain. A drain shall be located at the lowest point of the collection reservoir and shall be indirectly connected to the sanitary drainage system. The drain shall be the same diameter as the overflow pipe required in Section AO101.12.

AO101.14Vent required. The reservoir shall be provided with a vent sized in accordance with Chapter 31 of the Florida Building Code, Residential and based on the diameter of the reservoir influent pipe.

SECTION AO102 SYSTEMS FOR FLUSHING WATER CLOSETS AND URINALS

AO102.1 Collection reservoir. The holding capacity of the reservoir shall be a minimum of twice the volume of water required to meet the daily flushing requirements of the fixtures supplied with gray water, but not less than 50 gallons (189 L).  The reservoir shall be sized to limit the retention time of gray water to a maximum of 72 hours.

AO102.2 Disinfection. Gray water shall be disinfected by an approved method that employs one or more disinfectants such as chlorine, iodine or ozone.

AO102.3 Makeup water. Potable water shall be supplied as a source of makeup water for the gray water system. The potable water supply shall be protected against backflow in accordance with Section 608. There shall be a full-open valve located on the makeup water supply line to the collection reservoir.

AO102.4 Coloring. The gray water shall be dyed blue or green with a food grade vegetable dye before such water is supplied to the fixtures.

AO102.5 Materials. Distribution piping shall conform to one of the standards listed in Table 605.4.

AO102.6 Identification. Distribution piping and reservoirs shall be identified as containing nonpotable water. Piping identification shall be in accordance with Section 608.8.

Section AO 103 Subsurface Landscape Irrigation Systems.  Reserved

Delete figure AO101.1(1) and rename figure AO101.1(2) to figure AO101.1(1).

Appendix P Sizing of Water Piping System.  Change to read as shown.

Appendix P Sizing of Water Piping System.  Reserved.

Appendix Q:  ICC IRC Electrical Provisions/ National Electrical Code Cross-Reference.  Change to read as shown.

Appendix Q:  ICC IRC Electrical Provisions/ National Electrical Code Cross-Reference.  Reserved.