| FLORIDA ENERGY EFFICIENCY CODE FOR BUILDING CONSTRUCTION CHAPTER 5 – Building Envelope Prescriptive Method |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Form 502-2010 All Climate Zones |  |  |  |  |  |  |  |  |  |  |  |  |
| Project Name: |  |  |  |  | Buildings that may comply by this form: Shell buildings (preliminary), renovation, change of occupancy type permitted before 1979, limited or special use building, building system changeouts) |  |  |  |  |  |  |  |
| Address: |  |  |  |  |  |  |  |  |  |  |  |  |
| City, Zip Code: |  |  |  |  | Building Permit No.: |  |  |  |  |  |  |  |
| Builder: |  |  |  |  | Permitting Office: |  |  |  |  |  |  |  |
| Owner: |  |  |  |  | Jurisdiction No.: |  |  |  |  |  |  |  |
| BUILDING ENVELOPE INFORMATION |  |  |  |  |  |  |  |  |  |  |  |  |
| ENVELOPE COMPONENT |  |  | Shell building |  |  |  |  | Renovation; Change of occupancy type; Limited/Special Use building; Lighting or equipment changeout |  |  |  |  |
| Roof: Absorptance: R-value (U-value): |  |  |  |  |  |  |  |  |  |  |  |  |
| Wall: Above grade wall Absorptance: R-value (U- value): Below grade wall |  |  |  |  |  |  |  |  |  |  |  |  |
| Floor: Raised Floor Insulation: R-value (U-value): Slab-on-grade: No requirement unless heated: |  |  |  |  |  |  |  |  |  |  |  |  |
| Fenestration U- factor SHGC (by percent of wall area): Overhang Projection Factor (PF): |  |  |  |  |  |  |  | N.A. |  |  |  |  |
| Skylights: SHGC: U- factor: Percent of roof area: |  |  |  |  |  |  |  | N.A. |  |  |  |  |
| SYSTEMS INFORMATION (if applicable) |  |  |  |  |  |  |  |  |  |  |  |  |
| SYSTEM | Type (describe system) |  |  | Size (capacity) |  |  | Sizing calculation |  | Efficiency Rating |  |  |  |
| Air-conditioning system |  |  |  |  |  |  |  |  |  |  |  |  |
| Heating system |  |  |  |  |  |  |  |  |  |  |  |  |
| Ventilation |  |  |  | Fan Power: |  |  |  |  | CFM |  |  |  |
| Ducts | Location: |  |  |  |  |  |  |  | R-value |  |  |  |
| Piping | Fluid design operating temp: |  |  | Size of pipe: |  |  | ------- |  | Inches |  |  |  |
| Hot water |  |  |  |  |  |  | ------- |  | EF |  |  |  |
| Electric power | Drawings |  |  | Y N |  |  | Operations manual available upon completion: Y N |  |  |  |  |  |
| Motors | Open or enclosed |  |  |  |  |  | Poles & speed: |  |  | Horsepower |  |  |
| Lighting | Space type: |  |  |  |  |  | Lighting power density |  |  |  |  |  |
| PRESCRIPTIVE MEASURES |  |  |  |  |  |  |  |  |  |  |  |  |
| Components | Section | Requirements |  |  |  |  |  |  |  |  |  |  |
| Operations Manual | 303.3.1 | Operations manual provided to owner. |  |  |  |  |  |  |  |  |  |  |
| Air infiltration: Windows & Doors Joints/Cracks Dropped Ceiling Cavity | 502.3 | Per 402.4.4: Windows, skylights & sliding glass doors air infiltration ≤ .3 cfm/sq.ft. Swinging doors ≤ 0.5 cfm/sq.ft. To be caulked, gasketted, weatherstripped or otherwise sealed. Recessed lights IC-rated and labeled to ASTM E 283. Vented: seal & insulated ceiling. Unvented seal & insulate roof & side walls. |  |  |  |  |  |  |  |  |  |  |
| Dehumidification | 503.4.5 | Simultaneous heating/cooling prohibited, Exceptions. |  |  |  |  |  |  |  |  |  |  |
| HVAC Efficiency | 503.2.3 | Minimum efficiencies: Tables 503.2.3(1)-(10) |  |  |  |  |  |  |  |  |  |  |
| HVAC Controls | 503.2.4 | Zone controls prevent reheat (exceptions); separate thermostatic control per zone; combined HAC control 5°F deadband, Exceptions. |  |  |  |  |  |  |  |  |  |  |
| Ventilation | 503.2.5 | Outdoor air supply & exhaust ducts shall have dampers that automatically shut when systems or spaces served are not in use. Exhaust air energy recovery required for cooling systems (Exceptions). |  |  |  |  |  |  |  |  |  |  |
| HVAC Ducts | 503.2.7 | Air ducts, fittings, mechanical equipment & plenum chambers shall be mechanically attached, sealed, insulated & installed per Table 503.2.7.2. Fan power limitations. |  |  |  |  |  |  |  |  |  |  |
| Balancing | 503.2.9.1 | HVAC distribution system(s) tested & balanced. Report in construction documents. |  |  |  |  |  |  |  |  |  |  |
| Piping Insulation | 503.2.8 | HAC and service hot water. In accordance with Table 503.2.8. |  |  |  |  |  |  |  |  |  |  |
| Water Heaters | 504 | Performance requirements in accordance with Table 504.2. Heat trap required. |  |  |  |  |  |  |  |  |  |  |
| Swimming Pools | 504.7 | Cover on heated pools; Time switch (exceptions); Readily accessible on/off switch. |  |  |  |  |  |  |  |  |  |  |
| Lighting Controls | 505.2, 502.3 | Automatic control required for interior lighting in buildings >5,000 s.f.; Space control; Exterior photo sensor; Tandem wiring where 1-3 linear fluorescent lamps >30W. |  |  |  |  |  |  |  |  |  |  |
| I hereby certify that the plans and specifications covered by the calculation are in compliance with the Florida Energy Code. PREPARED BY: ________________________________DATE: _________ I hereby certify that this building is in compliance with the Florida Energy Code: OWNER AGENT: _______________________________DATE:________ |  |  |  |  |  | Review of plans and specifications covered by this calculation indicates compliance with the Florida Energy Code. Before construction is completed, this building will be inspected for compliance in accordance with Section 553.908, F.S. BUILDING OFFICIAL:________________________ DATE: ___________ |  |  |  |  |  |  |

| BUILDING ENVELOPE REQUIREMENTS |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| SHELL BUILDINGS |  |  | RENOVATIONS; CHANGE OF OCCUPANCY; LIMITED/SPECIAL USE BUILDING; LIGHTING OR EQUIPMENT CHANGEOUT1 |  |  |
| BUILDING COMPONENT | REQUIREMENT |  | BUILDING COMPONENT |  | REQUIREMENT |
| Roof: Absorptance R-value (U-value) | ≤ 0.22 R-40 (U≤0.025) |  | Roof: Absorptance U-value |  | ≤ 0.22 R-40 (U≤0.025) |
| Wall: Above grade wall Absorptance R-value (U- value) Below grade wall | ≤ 0.30 R-30 (U≤ 0.032) No requirement |  | Wall: Above grade wall Absorptance R-value (U- value) Below grade wall |  | ≤ 0.30 R-30 (U≤ 0.032) No requirement |
| Raised Floor Insulation: R-value (U-value): | R-30 (U ≤ 0.032) |  | Raised Floor Insulation: R-value (U-value): |  | R-30 (U ≤ 0.032) |
| Windows: U- factor SHGC (by window area)2 0-40% WW Ratio 40-50% WW Ratio > 50 % Not allowed Overhang Projection Factor (PF)3 | ≤ 0.45 0.25 0.19 0.5 |  | Windows: U- factor SHGC (by window area) 0-40% WW Ratio >40% WW Ratio |  | ≤ 0.45 0.25 0.19 |
| Skylights: SHGC U- factor Maximum percent of roof area | ≤ 0.19 ≤ 1.36 ≤ 3% |  | Skylights: SHGC U- factor |  | ≤ 0.19 ≤ 1.36 |
| Opaque Door U- value: Swinging Non-swinging | ≤ 0.70 ≤ 1.45 |  | Opaque Door U- value: Swinging Non-swinging |  | ≤ 0.70 ≤ 1.45 |
| BUILDING SYSTEM REQUIREMENTS |  |  |  |  |  |
| SHELL BUILDINGS: Lighting and HVAC must be sufficiently efficient to meet a Section 506 calculation for the entire space at time of build-out. |  |  | OTHER BUILDING: Replacement systems4 |  |  |
| HVAC Equipment |  |  |  |  |  |
| Air conditioner (0-65KBtuh) |  | 13.0 SEER | Heat pump (0 – 65 KBtuh) | 13.0 SEER/ 7.7 HSPF |  |
| Air conditioner (>65-135KBtuh) |  | 11.2 EER | Heat pump (>65 – 135 KBtuh) | 10.8 EER/3.3 COP |  |
| Air conditioner (>135-240 KBtuh) |  | 11.0 EER | Heat pump (>135-240 KBtuh) | 10.4 EER/3.2 COP |  |
| Air conditioner (>240-760 KBtuh) |  | 10.0 EER, 9.7 IPLV | Heat pump (>240 KBtuh) | 9.3 EER, 9.0 IPLV/3.1 COP |  |
| Air conditioner (> 760 KBtuh) |  | 9.7 EER, 9.4 IPLV |  |  |  |
|  |  |  | Gas furnace (0-225 KBtuh) | 80% AFUE |  |
| Service Hot Water |  |  | Gas furnace (>225 KBtuh) | 80% Ec |  |
| Gas storage ≤75,00 Btu/h, ≥20 gallons |  | 0.67-0.0019V EF |  |  |  |
| Gas storage > 75,000 Btu/h |  | 80% Et | Lighting | LPD for space type on Table 505.5.1.2. |  |
| Gas instantaneous |  | 80% Et |  |  |  |
| Electric storage ≤12 kW |  | 0.97 – 0.0032xV EF |  |  |  |
| Pipe insulation Diameter ≤ 1.5 inches Diameter > 1.5 inches |  | 0.5 inch 1.0 inch |  |  |  |

1 See FBC-EC Table 101.4.1; meet code for component being changed as applicable.

2 Building with greater than 50% WWR shall comply with Section 506.

3  PF  .5 =  Projection half the distance of window height.

4 Other types of replacement equipment shall meet the code minimum for that type of equipment in the applicable table of Section 503.2.3 and 504.2.