CHAPTER 3

DESIGN CRITERIA CLIMATE ZONES

SECTION 301

CLIMATE ZONES

301.1 General. Climate zones shown in from Figure 301.1 or Table 301.1 constitute the zones recognized for Florida by the International Energy Conservation Code. shall be used in determining the applicable requirements from Chapters 4 and 5. Locations not in Table 301.1 (outside the United States) shall be assigned a climate zone based on Section 301.3.  Prescriptive envelope compliance methods in this code, Section 402 (residential) and Section 502 (commercial) have no difference in compliance criteria by climate zone. Climate criteria for the performance-based code compliance methods, Section 405 (residential) and Section 506 (commercial), are determined by climate data from the weather data collection station nearest to the building’s location.

301.2 Warm humid counties. All Florida counties are considered Wwarm humid counties are identified in Table 301.1 by an asterisk.

FIGURE 301.1

CLIMATE ZONES

Reserved

TABLE 301.1

CLIMATE ZONES, MOISTURE REGIMES, AND WARM-HUMID DESIGNATIONS  BY STATE, COUNTY AND TERRITORY

Key:  A – Moist, Asterisk (*) indicates a warm-humid location.

| COUNTY | CLIMATE ZONE | COUNTY | CLIMATE ZONE | COUNTY | CLIMATE ZONE |
| --- | --- | --- | --- | --- | --- |
| Alachua | 2A* | Hardee | 2A* | Okeechobee | 2A* |
| Baker | 2A* | Hendry | 2A* | Orange | 2A* |
| Bay | 2A* | Hernando | 2A* | Osceola | 2A* |
| Bradford | 2A* | Highlands | 2A* | Palm Beach | 2A* |
| Brevard | 2A* | Hillsborough | 2A* | Pasco | 2A* |
| Broward | 1A* | Holmes | 2A* | Pinellas | 2A* |
| Calhoun | 2A* | Indian River | 2A* | Polk | 2A* |
| Charlotte | 2A* | Jackson | 2A* | Putnam | 2A* |
| Citrus | 2A* | Jefferson | 2A* | Santa Rosa | 2A* |
| Clay | 2A* | Lafayette | 2A* | Sarasota | 2A* |
| Collier | 2A* | Lake | 2A* | Seminole | 2A* |
| Columbia | 2A* | Lee | 2A* | St. Johns | 2A* |
| DeSoto | 2A* | Leon | 2A* | St. Lucie | 2A* |
| Dixie | 2A* | Levy | 2A* | Sumter | 2A* |
| Duval | 2A* | Liberty | 2A* | Suwannee | 2A* |
| Escambia | 2A* | Madison | 2A* | Taylor | 2A* |
| Flagler | 2A* | Manatee | 2A* | Union | 2A* |
| Franklin | 2A* | Marion | 2A* | Volusia | 2A* |
| Gadsden | 2A* | Martin | 2A* | Wakulla | 2A* |
| Gilchrist | 2A* | Miami-Dade | 1A* | Walton | 2A* |
| Glades | 2A* | Monroe | 1A* | Washington | 2A* |
| Gulf | 2A* | Nassau | 2A* |  |  |
| Hamilton | 2A* | Okaloosa | 2A* |  |  |

301.3 International climate zones. Reserved. The climate zone for any location outside the United States shall be determined by applying Table 301.3(1) and then Table 301.3(2).

TABLE 301.3(1)

INTERNATIONAL CLIMATE ZONE DEFINITIONS

Reserved

MAJOR CLIMATE TYPE DEFINITIONS

Warm-humid Definition—Moist (A) locations where either of the following wet-bulb temperature conditions shall occur during the warmest six consecutive months of the year: - 67oF (19.4oC) or higher for 3,000 or more hours; or - 73oF (22.8oC) or higher for 1,500 or more hours

Dry (B) Definition – Locations meeting the following criteria: Not marine and Pm< 0.44 x (TF – 19.5) [Pcm < 2.0 x (TC + 7) in SI units] Where: Pin = Annual precipitation in inches (cm) T = Annual mean temperature in oF (oC)

Moist (A) Definition – Locations that are not marine and not dry.

For SI: oC = [(oF) – 32]/1.8; 1 inch = 2.54 cm.

TABLE  301.3(2)

INTERNATIONAL CLIMATE ZONE DEFINITIONS

Reserved

| ZONE NUMBER | THERMAL CRITERIA |  |
| --- | --- | --- |
|  | IP Units | SI Units |
| 1 | 9000 < CDD50oF | 5000 < CDD 10 oC. |
| 2 | 6300 < CDD 50oF ≤ 9000 | 3500 < CDD 10 oC ≤ 5000 |

For SI: oC = [(oF) – 32]/1.8

SECTION 302

DESIGN CONDITIONS

302.1 Interior design conditions. The interior design temperatures used for heating and cooling load calculations shall be a maximum of 72ºF (22ºC) for heating and minimum of 75ºF (24ºC) for cooling.

SECTION 303

MATERIALS, SYSTEMS AND EQUIPMENT

303.1 Identification. Materials, systems and equipment shall be identified in a manner that will allow a determination of compliance with the applicable provisions of this code.

303.1.1 Building thermal envelope insulation. An R-value identification mark shall be applied by the manufacturer to each piece of building thermal envelope insulation 12 inches (305 mm) or greater in width. Alternately, the insulation installers shall provide a certification listing the type, manufacturer and R-value of insulation installed in each element of the building thermal envelope. For blown or sprayed insulation (fiberglass and cellulose), the initial installed thickness, settled thickness, settled R-value, installed density, coverage area and number of bags installed shall be listed on the certification. For sprayed polyurethane foam (SPF) insulation, the installed thickness of the areas covered and R-value of installed thickness shall be listed on the certification. The insulation installer shall sign, date and post the certification in a conspicuous location on the job site.

303.1.1.1 Blown or sprayed roof/ceiling insulation. The thickness of blown-in or sprayed roof/ceiling insulation (fiberglass or cellulose) shall be written in inches (mm) on markers that are installed at least one for every 300 square feet (28 m2) throughout the attic space. The markers shall be affixed to the trusses or joists and marked with the minimum initial installed thickness with numbers a minimum of 1 inch (25 mm) in height. Each marker shall face the attic access opening. Spray polyurethane foam thickness and installed R-value shall be listed on certification provided by the insulation installer

303.1.2 Insulation mark installation. Insulating materials shall be installed such that the manufacturer’s R-value mark is readily observable upon inspection.

303.1.3 Fenestration product rating. U-factors of fenestration products (windows, doors and skylights) shall be determined in accordance with NFRC 100 by an accredited, independent laboratory, and labeled and certified by the manufacturer. Products lacking such a labeled U-factor shall be assigned a default U-factor from Table 303.1.3(1) or 303.1.3(2). The solar heat gain coefficient (SHGC) of glazed fenestration products (windows, glazed doors and skylights) shall be determined in accordance with NFRC 200 by an accredited, independent laboratory, and labeled and certified by the manufacturer. Products lacking such a labeled SHGC shall be assigned a default SHGC from Table 303.1.3(3).

TABLE 303.1.3(1)

DEFAULT GLAZED FENESTRATION U-FACTOR

| Frame Type | Single Pane | Double pane | Skylight |  |
| --- | --- | --- | --- | --- |
|  |  |  | Single | Double |
| Metal | 1.20 | 0.80 | 2.00 | 1.30 |
| Metal with thermal break | 1.10 | 0.65 | 1.90 | 1.10 |
| Nonmetal or metal clad | 0.95 | 0.55 | 1.75 | 1.05 |
| Glazed block | 0.60 |  |  |  |

TABLE 303.1.3(2)

DEFAULT DOOR U-FACTORS

| Door Type | U-Factor |
| --- | --- |
| Uninsulated metal | 1.20 |
| Insulated metal | 0.60 |
| Wood | 0.50 |
| Insulated, nonmetal edge, max. 45% glazing, any glazing double pane | 0.35 |

TABLE 303.1.3(3)

DEFAULT GLAZED FENESTRATION SHGC

| Single Glazed |  | Double Glazed |  | Glazed Block |
| --- | --- | --- | --- | --- |
| Clear | Tinted | Clear | Tinted |  |
| 0.8 | 0.7 | 0.7 | 0.6 | 0.6 |

303.1.4 Insulation product rating. The thermal resistance (R-value) of insulation shall be determined in accordance with the U.S. Federal Trade Commission R-value rule (CFR Title 16, Part 460, May 31, 2005) in units of h ft2 °F/Btu at a mean temperature of 75°F (24°C).

303.2 Installation. All materials, systems and equipment shall be installed in accordance with the manufacturer’s installation instructions and the Florida International Building Code.

303.2.1 Protection of exposed foundation insulation. Insulation applied to the exterior of basement walls, crawlspace walls and the perimeter of slab-on-grade floors shall have a rigid, opaque and weather-resistant protective covering to prevent the degradation of the insulation’s thermal performance. The protective covering shall cover the exposed exterior insulation and extend a minimum of 6 inches (153 mm) below grade.

303.3 Maintenance information. Maintenance instructions shall be furnished for equipment and systems that require preventive maintenance. Required regular maintenance actions shall be clearly stated and incorporated on a readily accessible label. The label shall include the title or publication number for the operation and maintenance manual for that particular model and type of product.

303.3.1 Commercial buildings.  The code official shall ensure that the construction documents require an operating and maintenance manual be transmitted to the building owner for all commercial buildings. The manual shall include basic data relating to the design, operation and maintenance of HVAC and lighting systems and equipment. Required routine maintenance actions shall be clearly identified. Where applicable, control information such as diagrams, schematics, control sequence descriptions, and maintenance and calibration information shall be included.