Chapter 4

Residential Energy Efficiency

SECTION 401

GENERAL

401.1 Scope. This chapter applies to residential buildings

401.2 Compliance. Projects shall comply with Sections 401, 402.4, 402.5, and 403.1, 403.2.2, 403.2.3, and 403.3 through 403.9 (referred to as the mandatory provisions) and either:

1. Sections 402.1 through 402.3, 403.2.1 and 404.1 (prescriptive); or

2. Section 405 (performance).

401.3 Certificate. Energy performance level (EPL) display card. The building official shall require that an energy performance level (EPL) display card be completed and certified by the builder to be accurate and correct before final approval of the building for occupancy. Florida law (Section 553.9085, Florida Statutes) requires the EPL display card to be included as an addendum to each sales contract for both presold and nonpresold residential buildings. The EPL display card contains information indicating the energy performance level and efficiencies of components installed in a dwelling unit. The building official shall verify that the EPL display card completed and signed by the builder accurately reflects the plans and specifications submitted to demonstrate code compliance for the building. A copy of the EPL Display Card can be found in Appendix C. A permanent certificate shall be posted on or in the electrical distribution panel . The certificate shall not cover or obstruct the visibility of the circuit directory label, service disconnect label or other required labels. The certificate shall be completed by the builder or registered design professional. The certificate shall list the predominant R-values of insulation installed in or on ceiling/roof, walls, foundation (slab, basement wall, crawlspace wall and/or floor) and ducts outside conditioned spaces; U-factors for fenestration and the solar heat gain coefficient (SHGC) of fenestration. Where there is more than one value for each component, the certificate shall list the value covering the largest area. The certificate shall list the types and efficiencies of heating, cooling and service water heating equipment. Where a gas-fired unvented room heater, electric furnace, or baseboard electric heater is installed in the residence, the certificate shall list “gas-fired unvented room heater,” “electric furnace” or “baseboard electric heater,” as appropriate. An efficiency shall not be listed for gas-fired unvented room heaters, electric furnaces or electric baseboard heaters.

SECTION 402

BUILDING THERMAL ENVELOPE

402.1 General (Prescriptive).

402.1.1 Insulation and fenestration criteria. The building thermal envelope shall meet the requirements of Table 402.1.1 based on the climate zone specified in Chapter 3.

402.1.1.1.2 R-value computation. Insulation material used in layers, such as framing cavity insulation and insulating sheathing, shall be summed to compute the component R-value. The manufacturer’s settled R-value shall be used for blown insulation. Computed R-values shall not include an R-value for other building materials or air films.

TABLE 402.1.1

INSULATION AND FENESTRATION REQUIREMENTS BY COMPONENTa

COMPONENT EFFICIENCIES REQUIREDa,l

| Climate Zone % Glazingc | Fenestration U-Factorb | Sky-lightb U-Factor | Glazed Fenes- tration SHGCb,e | Ceiling R-value | Roof Reflectance Tested per S. 405.6.2 | Wood Frame Wall R-value | Mass Wall R-valuei | Floor R-value/ Slab R-valued | Basementc Wall R-value Door U-Factor | Slabd R-value & Depth Ducts: R-value/ Locationk | Crawl Spacec Wall R-value Air Handler Locationk, | Air Leakage Tested per S. 403.2.2.1 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 20% | 0.65 j | 0.75 | 0.30 | 30 | 0.25 | 13 | 6 / 7.8 | 13/0 | 0.65 | R-6/ Conditioned | Conditioned | Qn=0.03 |

For SI: 1 foot = 304.8 mm.

a. R-values are minimums. U-factors and SHGC are maximums. R-19 batts compressed into a nominal 2 × 6 framing cavity such that the R-value is reduced by R-1 or more shall be marked with the compressed batt R-value in addition to the full thickness R-value.

b. The fenestration U-factor column excludes skylights. The SHGC column applies to all glazed fenestration.

c. Percent glazing shown shall be the maximum glazing allowed for compliance by Section 402. Percent glazing area shall be measured in window to floor area and shall include skylight area. “15/19” means R-15 continuous insulated sheathing on the interior or exterior of the home or R-19 cavity insulation at the interior of the basement wall. “15/19” shall be permitted to be met with R-13 cavity insulation on the interior of the basement wall plus R-5 continuous insulated sheathing on the interior or exterior of the home. “10/13” means R-10 continuous insulated sheathing on the interior or exterior of the home or R-13 cavity insulation at the interior of the basement wall.

d. R-5 shall be added to the required slab edge R-values for heated slabs only;. Iinsulation depth shall be the depth of the footing or 2 feet, whichever is less in Zones 1through 3 for heated slabs. No insulation is required for unheated slabs, basement walls or crawl space walls.

e. Reserved There are no SHGC requirements in the Marine Zone.

f. Reserved. Basement wall insulation is not required in warm-humid locations as defined by Figure 301.1 and Table 301.1.

g. Or insulation sufficient to fill the framing cavity, R-19 minimum.

h. “13+5” means R-13 cavity insulation plus R-5 insulated sheathing. If structural sheathing covers 25 percent or less of the exterior, insulating sheathing is not required where structural sheathing is used. If structural sheathing covers more than 25 percent of exterior, structural sheathing shall be supplemented with insulated sheathing of at least R-2.

i. The second R-value applies when more than half the insulation is on the interior of the mass wall.

j. For impact rated fenestration complying with Section R301.2.1.2 of the International Florida Building Residential Code, Residential or Section 1609.1.2 of the International Florida Building Code, Building the maximum U-factor shall be 0.75 in Zone 2 and 0.65 in Zone 3.

k. Conditioned= entire distribution system located inside both the thermal and air barrier of the home.  Unconditioned = any portion located in unconditioned space.

l. Limitations to compliance by Section 402 found in Section 402.2 shall be met.

TABLE 402.1.1.3

EQUIVALENT U-FACTORSa,f,g

| Climate Zone | Fenestration U-Factore | Skylight U-Factor | Ceiling U-Factorh | Frame Wall U-Factor | Mass Wall U-Factorb | Floor U-Factor | Basement Wall U-Factord | Crawl Space Wall U-Factorc |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 1.20 | 0.75 | 0.035 | 0.082 | 0.197 | 0.064 | 0.360 | 0.477 |
| 2 | 0.65 | 0.75 | 0.035 | 0.082 | 0.124 | 0.064 | 0.360 | 0.477 |

a. Nonfenestration U-factors shall be obtained from measurement, calculation or an approved source.

b. When more than half the insulation is on the exterior interior, the mass wall U-factors shall be a maximum of  0.165.  0.17 in Zone 1, 0.14 in Zone 2, 0.12 in Zone 3, 0.10 in Zone 4 except Marine, and the same as the frame wall U-factor in Marine Zone 4 and Zones 5 through 8.

c. Basement wall U-factor of 0.360 in warm-humid locations as defined by Figure 301.1 and Table 301.2.

d. Foundation U-factor requirements shown in Table 402.1.3 include wall construction and interior air films but exclude soil conductivity and exterior air films. U-factors for determining code compliance in accordance with Section 402.1.1.2 4 (total UA alternative) of Section 405 (Simulated Performance Alternative) shall be modified to include soil conductivity and exterior air films.

e. Window to floor area, including skylights, shall not exceed 20 percent. See Section 402.1.2.3.

f. Limitations to compliance by Section 402 found in Section 402.2 shall be met.

g. Ducts and air handlers shall be located inside both the thermal and air barrier of the home. Air leakage shall be no more than Qn=0.03 when tested per Section 403.2.2.1.

h. Roof reflectance shall be no more than 0.25 in accordance with testing to Section 405.5.5.2.

402.1.1.2. 3 U-factor alternative. An assembly with a U-factor equal to or less than that specified in Table 402.1.3 shall be permitted as an alternative to the corresponding component R-value in Table 402.1.1. All other prescriptive criteria of Table 402.1.1, the prescriptive criteria in Section 402.1.5 and footnotes to Table 402.1.1.3 shall be met.

402.1.1.3 4 Total UA alternative. If the total building thermal envelope UA (sum of U-factor times assembly area) is less than or equal to the total UA resulting from using the U-factors in Table 402.1.3 (multiplied by the same assembly area as in the proposed building), the building shall be considered in compliance with Table 402.1.1. All other prescriptive criteria of Table 402.1.1, the prescriptive criteria in Section 402.1.5 and footnotes to Table 402.1.1.3 shall be met. The UA calculation shall be done using a method consistent with the ASHRAE Handbook of Fundamentals and shall include the thermal bridging effects of framing materials. The SHGC requirements shall be met in addition to UA compliance.

402.1.2 Limitations to compliance by Section 402.

402.1.2.1 Electric space heating. Electric resistance space heating systems shall not be used when complying with this code by Section 402.

402.1.2.2 Air handlers in attics. Air handlers may not be installed in attics when complying with Section 402.

402.1.2.3 Maximum percent window area.  The window area as a percentage of the conditioned floor area (CFA) shall not exceed 20 percent.

Exceptions: The following exceptions apply to additions.

1. When a fenestration(s) in an existing exterior wall is being removed or enclosed by an addition, an amount equal to the total area of this fenestration may be subtracted from the total glass area prior to determining the installed glass percentage.

2. Additions of 600 square feet (56 m2) or less may have up to 50 percent glass to conditioned floor area.

3. Glass windows and doors that were previously located in an existing exterior wall that is being removed or enclosed by an addition do not have to comply with the U-factor and solar heat gain coefficient requirements in Table 402.1.1 when reinstalled as part of the addition.

402.1.2.5 Equipment efficiencies. Minimum equipment efficiencies for cooling, heating and water heating shall be code minimums as per Sections 503.

402.2 Specific insulation requirements (Prescriptive).

402.2.1Ceilings with attic spaces. Reserved. When Section 402.1.1 would require R-38 in the ceiling, R-30 shall be deemed to satisfy the requirement for R-38 wherever the full height of uncompressed R-30 insulation extends over the wall top plate at the eaves. Similarly, R-38 shall be deemed to satisfy the requirement for R-49 wherever the full height of uncompressed R-38 insulation extends over the wall top plate at the eaves. This reduction shall not apply to the U-factor alternative approach in Section 402.1.1.2 402.1.3 and the total UA alternative in Section 402.1.1.3 402.1.4.

402.2.2 Ceilings without attic spaces.  Where Section 402.1.1 would require insulation levels above R-30 and the design of the roof/ceiling assembly does not allow sufficient space for the required insulation, the minimum required insulation for such roof/ceiling assemblies shall be R-30. This reduction of insulation from the requirements of Section 402.1.1 shall be limited to 500 square feet (46m2) or 20 percent of the total insulated ceiling area, whichever is less. This reduction shall not apply to the U-factor alternative approach in Section 402.1.1.2 3 and the total UA alternative in Section 402.1.1.3 4

402.2.3 Access hatches and doors. Access doors from conditioned spaces to unconditioned spaces (e.g., attics and crawl spaces) shall be weatherstripped and insulated to a level equivalent to the insulation on the surrounding surfaces. Access shall be provided to all equipment that prevents damaging or compressing the insulation. A wood framed or equivalent baffle or retainer is required to be provided when loose fill insulation is installed, the purpose of which is to prevent the loose fill insulation from spilling into the living space when the attic access is opened, and to provide a permanent means of maintaining the installed -value of the loose fill insulation.

402.2.4 Mass walls. Mass walls for the purposes of this chapter shall be considered above-grade walls of concrete block, concrete, insulated concrete form (ICF), masonry cavity, brick (other than brick veneer), earth (adobe, compressed earth block, rammed earth) and solid timber/logs.

402.2.5 Steel-frame ceilings, walls, and floors. Steel frame ceilings, walls and floors shall meet the insulation requirements of Table 402.2.5 or shall meet the U-factor requirements in Table 402.1.1.3. The calculation of the U-factor for a steel-frame envelope assembly shall use a series-parallel path calculation method.

Exception: In Climate Zones 1 and 2, the continuous insulation requirements in Table 402.2.54 shall be permitted to be reduced to R-3 for steel frame wall assemblies with studs spaced at 24 inches (610 mm) on center.

402.2.6 Floors. Floor insulation shall be installed to maintain permanent contact with the underside of the subfloor decking.

402.2.7 Basement walls. Walls associated with conditioned basements shall be insulated from the top of the basement wall down to 10 feet (3048 mm) below grade or to the basement floor, whichever is less. Walls associated with unconditioned basements shall meet this requirement unless the floor overhead is insulated in accordance with Sections 402.1.1 and 402.2.6.

TABLE 402.2.5

STEEL-FRAME CEILING, WALL AND FLOOR INSULATION

(R-VALUE)

| Wood Frame R-Value Requirement | Cold-Formed Steel Equivalent R-valuea |
| --- | --- |
| Steel Truss Ceilingsb |  |
| R-30 | R-38 or R-30 + 3 or R-26 + 5 |
| R-38 | R-49 or R-38 + 3 |
| R-49 | R-38 + 5 |
| Steel Joist Ceilingsb |  |
| R-30 | R-38 in 2x4 or 2x6 or 2x8 R-49 in any framing |
| R-38 | R-49 in 2x4 or 2x6 or 2x8 or 2x10 |
| Steel-Framed Wall |  |
| R-13 | R-13 + 5 or R-15 + 4 or R-21 + 3 or R-0 + 10 |
| R-19 | R-13 + 9 or R-19 + 8 or R-25 + 7 |
| R-21 | R-13 + 10 or R-19 + 9 or R-25 + 8 |
| Steel Joist Floor |  |
| R-13 | R-19 in 2x6 R-19 + 6 in 2x8 or 2x10 |
| R-19 | R-19 + 6 in 2x6 R-19 + 12 in 2x8 or 2x10 |

a. Cavity insulation R- value is listed first, followed by continuous insulation R- value.

b. Insulation exceeding the height of the framing shall cover the framing.

402.2.8 Slab-on-grade floors. Reserved.  Slab-on-grade floors with a floor surface less than 12 inches (305 mm) below grade shall be insulated in accordance with Table 402.1.1. The insulation shall extend downward from the top of the slab on the outside or inside of the foundation wall. Insulation located below grade shall be extended the distance provided in Table 402.1.1 by any combination of vertical insulation, insulation extending under the slab or insulation extending out from the building. Insulation extending away from the building shall be protected by pavement or by a minimum of 10 inches (254 mm) of soil. The top edge of the insulation installed between the exterior wall and the edge of the interior slab shall be permitted to be cut at a 45-degree (0.79 rad) angle away from the exterior wall. Slab-edge insulation is not required in jurisdictions designated by the code official as having a very heavy termite infestation.

402.2.9 Crawl space walls. As an alternative to insulating floors over crawl spaces, crawl space walls shall be permitted to be insulated when the crawl space is not vented to the outside. Crawl space wall insulation shall be permanently fastened to the wall and extend downward from the floor to the finished grade level and then vertically and/or horizontally for at least an additional 24 inches (610 mm). Exposed earth in unvented crawl space foundations shall be covered with a continuous Class I vapor retarder. All joints of the vapor retarder shall overlap by 6 inches (153 mm) and be sealed or taped. The edges of the vapor retarder shall extend at least 6 inches (153 mm) up the stem wall and shall be attached to the stem wall.

402.2.10 Masonry veneer. Insulation shall not be required on the horizontal portion of the foundation that supports a masonry veneer.

402.2.11 Thermally isolated sunroom insulation. The minimum ceiling insulation R-values shall be R-19 in Zones 1 through 4 and R-24 in Zones 5 through 8. The minimum wall R-value shall be R-13 in all zones. New wall(s) separating a sunroom from conditioned space shall meet the building thermal envelope requirements

402.2.12 Common walls/ceilings/floors. Walls, ceilings or floors common to separate conditioned tenancies shall be insulated to a minimum R-11, space permitting.

Exception:  Mass common walls shall be insulated to a minimum of R-6.

402.2.13  Walls considered ceiling area. Wall areas that separate conditioned living space from unconditioned attic space (such as attic knee walls, walls on cathedral ceilings, skylight chimney shafts, gambrel roofs, etc.) shall be considered ceiling area. Such areas shall be included in calculations of ceiling area and shall have a minimum insulation value of R-19.

402.3 Fenestration. (Prescriptive).

402.3.1 U-factor. An area-weighted average of fenestration products shall be permitted to satisfy the U-factor requirements.

402.3.2 Glazed fenestration SHGC. An area-weighted average of fenestration products more than 50 percent glazed shall be permitted to satisfy the SHGC requirements

402.3.3 Glazed fenestration exemption. Up to 15 square feet (1.4m2) of glazed fenestration per dwelling unit shall be permitted to be exempt from U-factor and SHGC requirements in Section 402.1.1. This exemption shall not apply to the U-factor alternative approach in Section 402.1.1.2 3 and the Total UA alternative in Section 402.1.1.3 4.

402.3.4 Opaque door exemption. One side-hinged opaque door assembly up to 24 square feet (2.22 m2) in area is exempted from the U-factor requirement in Section 402.1.1. This exemption shall not apply to the U-factor alternative approach in Section 402.1..1.2 3 and the total UA alternative in Section 402.1.1.3 4

402.3.5 Thermally isolated sunroom U-factor. For Zones 4 through 8, the maximum fenestration U-factor shall be 0.50 and the maximum skylight U-factor shall be 0.75. New windows and doors separating the sunroom from conditioned space shall meet the building thermal envelope requirements.

402.3.6 Replacement fenestration. Where some or all of an existing fenestration unit is replaced with a new fenestration product, including sash and glazing, the replacement fenestration unit shall meet the applicable requirements for U-factor and SHGC in Table 402.1.1.

402.4 Air leakage (Mandatory).

402.4.1 Building thermal envelope. The building thermal envelope shall be durably sealed to limit infiltration. The sealing methods between dissimilar materials shall allow for differential expansion and contraction. The following shall be caulked, gasketed, weatherstripped or otherwise sealed with an air barrier material, suitable film or solid material:

1. All joints, seams and penetrations.

2. Site-built windows, doors and skylights.

3. Openings between window and door assemblies and their respective jambs and framing.

4. Utility penetrations.

5. Dropped ceilings or chases adjacent to the thermal envelope.

6. Knee walls.

7. Walls and ceilings separating a garage from conditioned spaces.

8. Behind tubs and showers on exterior walls.

9. Common walls between dwelling units.

10. Attic access openings.

11. Rim joist junction.

12. Other sources of infiltration.

402.4.2 Air sealing and insulation. Building envelope air tightness and insulation installation shall be demonstrated to comply with one of the following options given by Section 402.4.2.1 or 402.4.2.2

402.4.2.1 Testing option. Building envelope tightness and insulation installation shall be considered acceptable when tested air leakage is less than seven air changes per hour (ACH) when tested with a blower door at a pressure of 33.5 psf (50 Pa). Testing shall occur after rough in and after installation of penetrations of the building envelope, including penetrations for utilities, plumbing, electrical, ventilation and combustion appliances.

During testing:

1. Exterior windows and doors, fireplace and stove doors shall be closed, but not sealed;

2. Dampers shall be closed, but not sealed, including exhaust, intake, makeup air, backdraft and flue dampers;

3. Interior doors shall be open;

4. Exterior openings for continuous ventilation systems and heat recovery ventilators shall be closed and sealed;

5. Heating and cooling system(s) shall be turned off;

6. HVAC ducts shall not be sealed; and

7. Supply and return registers shall not be sealed.

402.4.2.2 Visual inspection option. Building envelope tightness and insulation installation shall be considered acceptable when the items listed in Table 402.4.2, applicable to the method of construction, are field verified. Where required by the code official, an approved party independent from the installer of the insulation shall inspect the air barrier and insulation.	[No change to Table 402.4.2]

402.4.3 Fireplaces. New wood-burning fireplaces shall have gasketed doors and outdoor combustion air.

402.4.4 Fenestration air leakage. Windows, skylights and sliding glass doors shall have an air infiltration rate of no more than 0.3 cfm per square foot (1.5 L/s/m2), and swinging doors no more than 0.5 cfm per square foot (2.6 L/s/m2), when tested according to NFRC 400 or AAMA/WDMA /CSA 101/I.S.2/A440 by an accredited, independent laboratory and listed and labeled by the manufacturer.

Exceptions: Site-built windows, skylights and doors.

402.4.5 Recessed lighting. Recessed luminaires installed in the building thermal envelope shall be sealed to limit air leakage between conditioned and unconditioned spaces. All recessed luminaires shall be IC-rated and labeled as meeting ASTM E 283 when tested at 1.57 psf (75 Pa) pressure differential with no more than 2.0 cfm (0.944 L/s) of air movement from the conditioned space to the ceiling cavity.

All recessed luminaires shall be sealed with a gasket or caulk between the housing and the interior wall or ceiling covering.

402.5 Maximum fenestration U-factor and SHGC (Mandatory). The area-weighted average maximum fenestration U-factor permitted using trade-offs from Section 402.1.4 or 404 shall be 0.48 in Zones 4 and 5 and 0.40 in Zones 6 through 8 for vertical fenestration, and 0.75 in Zones 4 through 8 for skylights. The area-weighted average maximum fenestration SHGC permitted using trade-offs from Section 405 in Zones 1 through 3 shall be 0.50.

SECTION 403

SYSTEMS

403.1 Controls (Mandatory). At least one thermostat shall be provided for each separate heating and cooling system.

403.1.1 Programmable thermostat. Where the primary heating system is a forced-air furnace, at least one thermostat per dwelling unit capable of controlling the heating and cooling system on a daily schedule to maintain different temperature set points at different times of the day. This thermostat shall include the capability to set back or temporarily operate the system to maintain zone temperatures down to 55°F (13°C) or up to 85°F (29°C). The thermostat shall initially be programmed with a heating temperature set point no higher than 70°F (21°C) and a cooling temperature set point no lower than 78°F (26°C).

403.1.2 Heat pump supplementary heat (Mandatory). Heat pumps having supplementary electric-resistance heat shall have controls that, except during defrost, prevent supplemental heat operation when the heat pump compressor can meet the heating load.

403.1.3 Humidity control. Where a humidistat is used for comfort dehumidification, it shall be capable of being set to prevent the use of fossil fuel or electricity to reduce humidities below 60 percent.

403.2  Ducts.

403.2.1 Insulation (Prescriptive). Supply ducts, including air filter enclosures, air ducts and plenums, located in attics or on roofs shall be insulated to a minimum of R-8. All other ducts shall be insulated to a minimum of R-6.

Exceptions:

1. Ducts or portions thereof located completely inside the building thermal envelope.

2. Exhaust air ducts

3. Factory-installed plenums, casings or ductwork furnished as a part of tested and rated HVAC equipment.

403.2.2 Sealing (Mandatory). All ducts, air handlers, filter boxes and building cavities which form the primary air containment passageways for air distribution systems shall be considered ducts or plenum chambers, shall be constructed and sealed in accordance with used as ducts shall be sealed. Joints and seams shall comply with Section 503.2.7.2 of this code M1601.4.1 of the International Residential, Code  and shall be shown to meet duct tightness criteria in Section 403.2.2.1.

.403.2.2.1 Duct tightness.  Duct tightness shall be verified by testing to either of the following

1. Post construction test: Leakage to outdoors shall be less than or equal to 8 cfm (226.5 L/min) per 100 ft2 (9.29 m2) of conditioned floor area or a total leakage less than or equal to 12 cfm (12 L/min) per 100 ft2 (9.29 m2) of conditioned floor area when tested at a pressure differential of 0.1 inches w.g. (25 Pa) across the entire system, including the manufacturer’s air handler enclosure. All register boots shall be taped or otherwise sealed during the test.

2. Rough-in test:  Total leakage shall be less than or equal to 6 cfm (169.9 L/min) per 100 ft2 (9.29 m2) of conditioned floor area when tested at a pressure differential of 0.1 inches w.g. (25 Pa) across the roughed-in system, including the manufacturer’s air handler enclosure. All register boots shall be taped or otherwise sealed during the test. If the air handler is not installed at the time of the test, total leakage shall be less than or equal to 4 cfm (113.3 L/min) per 100 ft2 (9.29 m2) of conditioned floor area.

Exceptions: Duct tightness test is not required if the air handler and all ducts are located within conditioned space. ASHRAE Standard 152. All ducts and air handlers shall be either located in conditioned space or tested by a Class 1 BERS rater to be “substantially leak free”.

403.2.3 Building cavities. Building framing cavities shall not be used as supply ducts.

403.2.4 Air-handling units.  Air handling units shall not be installed in the attic when a home is brought into code compliance by Section 402. Air-handling units shall be allowed in attics  for compliance by Section 405 only if the following conditions are met:

1.  The service panel of the equipment is located within 6 feet (1829 mm) of an attic access.

2.  A device is installed to alert the owner or shut the unit down when the condensation drain is not working properly.

3.  The attic access opening is of sufficient size to replace the air handler.

4.  A notice is posted on the electric service panel indicating to the homeowner that the air handler is located in the attic. Said notice shall be in all capitals, in 16 point type, with the title and first paragraph in bold:

NOTICE TO HOMEOWNER

A PART OF YOUR AIR-CONDITIONING SYSTEM, THE AIR HANDLER, IS LOCATED IN THE ATTIC. FOR PROPER, EFFICIENT, AND ECONOMIC OPERATION OF THE AIR-CONDITIONING SYSTEM, YOU MUST ENSURE THAT REGULAR MAINTENANCE IS PERFORMED.  YOUR AIR-CONDITIONING SYSTEM IS EQUIPPED WITH ONE OR BOTH OF THE FOLLOWING: (1) A DEVICE THAT WILL ALERT YOU WHEN THE CONDENSATION DRAIN IS NOT WORKING PROPERLY OR (2) A DEVICE THAT WILL SHUT THE SYSTEM DOWN WHEN THE CONDENSATION DRAIN IS NOT WORKING. TO LIMIT POTENTIAL DAMAGE TO YOUR HOME, AND TO AVOID DISRUPTION OF SERVICE, IT IS RECOMMENDED THAT YOU ENSURE PROPER WORKING ORDER OF THESE DEVICES BEFORE EACH SEASON OF PEAK OPERATION.

403.3 Mechanical system piping insulation (Mandatory). Mechanical system piping capable of carrying fluids above 105°F (41°C) or below55°F (13°C) shall be insulated to a minimum of R-3.

403.4 Hot water systems (Mandatory)

403.4.1 Circulating hot water systems, insulation (Mandatory). All circulating service hot water piping shall be insulated to at least R-2. Circulating hot water systems shall include an automatic or readily accessible manual switch that can turn off the hot water circulating pump when the system is not in use. Pipe insulation buried underground shall be as specified by the manufacturer for underground use.

403.4.2  Heat traps. Storage water heaters not equipped with integral heat traps and having vertical pipe risers shall have heat traps installed on both the inlets and outlets. External heat traps shall consist of either a commercially available heat trap or a downward and upward bend of at least 3½ inches (89 mm) in the hot water distribution line and cold water line located as close as possible to the storage tank.

403.4.3 Water heater efficiencies.

403.4.3.1 Storage water heater temperature controls.

403.4.3.1.1 Automatic controls. Service water heating systems shall be equipped with automatic temperature controls capable of adjustment from the lowest to the highest acceptable temperature settings for the intended use. The minimum temperature setting range shall be from 100°F to 140°F (38°C to 60°C).

403.4.3.1.2 Shut down. A separate switch or a clearly marked circuit breaker shall be provided to permit the power supplied to electric service systems to be turned off. A separate valve shall be provided to permit the energy supplied to the main burner(s) of combustion types of service water heating systems to be turned off.

403.4.3.2  Water heater efficiencies.  Residential sized water heaters shall meet the minimum efficiencies of this section. Water heating systems not covered in this section shall meet the minimum efficiencies listed for that system in Section 504 of this code.

403.4.3.2.1 Electric water heaters.  All automatic electric storage water heaters having a storage capacity of 120 gallons (454 L) or less and an input rating of 12 kw or less shall, when tested in accordance with the DOE Uniform Test Method for Measuring the Energy Consumption of Water Heaters, Appendix E to Subpart B, 10 CFR Part 430, meet the performance minimums listed in Table 403.4.3.2.

403.4.3.2.2  Gas- and oil-fired water heater efficiencies. All gas- and oil-fired automatic storage water heaters with capacities of 100 gallons or less and an input rating of 75,000 Btu/h or less (gas) or 105,000 Btu/h or less (oil) shall, when tested in accordance with the DOE Uniform Test Method for Measuring the Energy Consumption of Water Heaters, Appendix E to Subpart B, 10 CFR Part 430, meet the performance minimums listed in Table 403.4.3.2.

403.4.3.2.2.1  Gas Instantaneous or Tankless Water Heaters.   All gas-fired instantaneous (tankless) water heaters that a) initiate heating based on sensing water flow, b) are designed to deliver water at a controlled temperature of less than 180 °F (82 °C), c) have an input less than 200,000 Btu/h (210 MJ/h), d) have a manufacturer's specified storage capacity of less than 2 gallons (7.6 liters) and, e) have either a fixed or variable burner input shall, when tested in accordance with the DOE Uniform Test Method for Measuring the Energy Consumption of Water Heaters, Appendix E to Subpart B, Title 10 CFR 430, meet the performance minimums established in Title 10 CFR 430.32, Energy and Water Conservation Standards and Effective Dates.

403.4.3.2.2.2 Combination service water heating and space heating equipment. Service water heating equipment used to provide additional functions (e.g. space heating) as part of a combination (integrated) system shall comply with minimum performance requirements for water heating equipment.  For combined gas storage tank water heating and space heating systems tested to ANSI/ASHRAE 124, the EF used shall be the effective water heating efficiency (CA ef) listed for the appliance by the Gas Appliance Manufacturer’s Association (GAMA).  For combined gas instantaneous (tankless) water heating and space heating systems, the EF used shall be determined in accordance with the DOE Uniform Test Method for Measuring the Energy Consumption of Water Heaters, Appendix E to Subpart B, Title 10 CFR 430.

Combination systems utilizing a storage tank water heater as the heat source for space heating purposes with input ratings of 105,000 Btu/h (360m3/kW) or less shall utilize a water heater listed by the Gas Appliance Manufacturer’s Association (GAMA). Changeouts of burners or heating elements to increase capacity shall not be made unless the unit has been listed at that capacity by GAMA.

403.4.3.2.3 Solar water heating systems. Solar systems for domestic hot water production are rated by the annual solar energy factor of the system. The solar energy factor of a system shall be determined from the Florida Solar Energy Center Directory of Certified Solar Systems. Solar collectors shall be tested in accordance with ISO Standard 9806, Test Methods for Solar Collectors, and SRCC Standard TM-1, Solar Domestic Hot Water System and Component Test Protocol. Collectors in installed solar water heating systems should meet the following criteria:

1. 	Be installed with a tilt angle between 10 degrees and 40 degrees of the horizontal; and

2. 	Be installed at an orientation within 45 degrees of true south.

TABLE 403.4.3.2

MINIMUM PERFORMANCE STANDARDS WATER HEATING EQUIPMENT:

FIRED STORAGE WATER HEATER MINIMUM ENERGY FACTORS (EF)

| TYPE / VOLUME | TANK VOLUME (GALLONS) |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 100 | 120 |
| ELECTRIC: Up to 120 gallon or 12kW input | .94 | .93 | .92 | .90 | .88 | — | .86 | .84 | .81 |
| GAS: Up to 100 gallon or 75,000 Btu/h input | .63 | .61 | .59 | .58 | .55 | .53 | — | .48 | — |
| OIL: Up to 50 gallon or 75,000 Btu/h input | — | .53 | .51 | .50 | — | — | — | — | — |

403.5 Mechanical ventilation (Mandatory). Outdoor air intakes and exhausts shall have automatic or gravity dampers that close when the ventilation system is not operating.

403.5.1 Ventilation air.  Residential buildings designed to be operated at a positive indoor pressure or for mechanical ventilation shall meet the following criteria:

1.  The design air change per hour minimums for residential buildings in ASHRAE 62, Ventilation for Acceptable Indoor Air Quality, shall be the maximum rates allowed for residential applications.

2.  No ventilation or air-conditioning system make-up air shall be provided to conditioned space from attics, crawlspaces, attached enclosed garages or outdoor spaces adjacent to swimming pools or spas.

3.  If ventilation air is drawn from enclosed space(s), then the walls of the space(s) from which air is drawn shall be insulated to a minimum of R-11 and the ceiling shall be insulated to a minimum of R-19, space permitting, or R-10 otherwise.

403.6 Heating and Cooling Equipment sizing (Mandatory).

403.6.1 Equipment sizing. Heating and cooling equipment shall be sized based on building loads for the directional orientation of the building for which the load is calculated, in accordance with ACCA Manual J or other approved heating and cooling calculation methodologies. in accordance with Section M1401.3 of the International Residential Code. The manufacturer and model number of the outdoor and indoor units (if split system) shall be submitted along with the sensible and total cooling capacities at the design conditions described in Section 302.1.

403.6.1.1 Cooling equipment capacity. Cooling only equipment shall be selected so that its total capacity is not less than the calculated total load but not more than 1.15 times greater than the total load calculated according to the procedure selected in Section 403.6, or the closest available size provided by the manufacturer's product lines. The corresponding latent capacity of the equipment shall not be less than the calculated latent load.

Exceptions:

1.  Attached single- and multiple-family residential equipment sizing may be selected so that its cooling capacity is less than the calculated total sensible load but not less than 80 percent of that load.

2.  When signed and sealed by a Florida-registered engineer, in attached single- and multiple-family units, the capacity of equipment may be sized in accordance with good design practice.

Manufacturer’s expanded performance data shall be used to select cooling-only equipment. The published value for AHRI total capacity is a nominal, rating-test value and shall not be used for equipment sizing.

403.6.1.2 Heating equipment capacity.

403.6.1.2.1  Heat Pumps.  Heat pump sizing shall be based on the cooling requirements as calculated according to Section 403.6.1.1 and the heat pump total cooling capacity shall not be more than 1.15 times greater than the design cooling load even if the design heating load is 1.15 times greater than the design cooling load.

403.6.1.2.2  Electric resistance furnaces.  Electric resistance furnaces shall be sized within 4 kW of the design requirements calculated according to the procedure selected in Section 403.6.1.

403.6.1.2.3 Fossil fuel heating equipment.  The capacity of fossil fuel heating equipment with natural draft atmospheric burners shall not be less than the design load calculated in accordance with Section 403.6.1.

403.6.1.3 Extra capacity required for special occasions. Residences requiring excess cooling or heating equipment capacity on an intermittent basis, such as anticipated additional loads caused by major entertainment events, shall have equipment sized or controlled to prevent continuous space cooling or heating within that space by one or more of the following options:

1.  A separate cooling or heating system is utilized to provide cooling or heating to the major entertainment areas.

2.  A variable capacity system sized for optimum performance during base load periods is utilized.

403.6.2 Equipment performance standards.

403.6.2.1 Equipment ratings. Equipment efficiency ratings shall be obtained from a nationally recognized certification program directory, or from a manufacturer’s rating certified to be in compliance with an approved Department of Energy (DOE) or Air-conditioning, Heating and Refrigeration Institute (AHRI) rating procedure. Equipment efficiencies shall be based on the standard rating conditions contained in the test standard referenced in Chapter 6 that is appropriate for that equipment. Minimum ratings for products covered under the National Appliance Energy Conservation Act of 1987 shall be those determined for Region IV and used for the Federal Trade Commission’s required appliance labeling.

403.6.2.1.1 Equipment efficiency verification.  Equipment covered under the Federal Energy Policy Act of 1992 (EPACT) shall comply with U.S. Department of Energy certification requirements. For other equipment, if a certification program exists for a product covered in Table503.2.3, and it includes provisions for verification and challenge of equipment efficiency ratings, then the product shall be either listed in the certification program or, alternatively, the ratings shall be verified by an independent laboratory test report. If no certification program exists for a product covered in Tables 503.2.3, the equipment efficiency ratings shall be supported by data furnished by the manufacturer. Where components such as indoor or outdoor coils from different manufacturers are used, a Florida-registered engineer shall specify component efficiencies whose combined efficiency meets the minimum equipment efficiency requirements.

403.6.2.2 Minimum efficiencies for cooling equipment.  Cooling equipment installed in residential units shall meet the minimum efficiencies of Tables 503.2.3(1) through 503.2.3(3) and 503.2.3(6) through 503.2.3(9)  in Chapter 5 of this code for the type of equipment installed. Equipment used to provide water heating functions as part of a combination system shall satisfy all stated requirements for the appropriate space heating or cooling category.

Exception:  Existing mechanical systems undergoing alteration need not meet the minimum equipment efficiencies of this section except to preserve the original approval or listing of the equipment.

403.6.2.3 Minimum efficiencies for heating equipment. Heating equipment installed in residential units shall meet the minimum efficiencies of Tables 503.2.3(2) through 503.2.3(5) of Chapter 5 of this code for the type of equipment installed.

Exception:  Existing mechanical systems undergoing alteration need not meet the minimum equipment Efficiencies of this section except to preserve the original approval or listing of the equipment

403.6.2.3.1 Gas and oil-fired furnaces. Gas-fired and oil-fired forced air furnaces with input ratings >225,000 Btu/h shall also have an intermittent ignition or interrupted device (IID) and have either power venting or a flue damper. A vent damper is an acceptable alternative to a flue damper for furnaces where combustion air is drawn from the conditioned space. All furnaces with input ratings >225,000 Btu/h, including electric furnaces, that are not located within the conditioned space shall have jacket losses not exceeding 0.75 percent of the input.

403.6.2.3.2 Central electric furnaces. Central electric furnaces greater than 10 kW shall be divided into at least two stages and controlled by an outdoor thermostat, multistage indoor thermostat, or combinations thereof.

403.7 Systems serving multiple dwelling units (Mandatory). Systems serving multiple dwelling units shall comply with Sections 503 and 504 in lieu of Section 403.

403.8 Snow melt system controls (Mandatory). Reserved.  Snow- and ice-melting systems, supplied through energy service to the building, shall include automatic controls capable of shutting off the system when the pavement temperature is above 50°F, and no precipitation is falling and an automatic or manual control that will allow shutoff when the outdoor temperature is above 40°F.

403.9 Pools (Mandatory). Pools shall be provided with energy-conserving measures in accordance with Sections 403.9.1 through 403.9.43.

403.9.1 Pool and spa heaters. All pool heaters shall be equipped with a readily accessible on-off switch that is mounted outside the heater to allow shutting off the heater without adjusting the thermostat setting.

403.9.1.1 Gas and oil-fired pool and spa heaters. All gas- and oil-fired pool and spa heaters shall have a minimum thermal efficiency of 78 percent when tested in accordance with ANSI Z 21.56.  Pool heaters fired by natural gas shall not have continuously burning pilot lights. 
 403.9.1.2 Heat pump pool heaters.  Heat pump pool heaters shall have a minimum COP of 4.0 when tested in accordance with ARI 1160, Table 2, Standard Rating Conditions-Low Air Temperature. A test report from an independent laboratories is required to verify procedure compliance.

403.9.1.3 Portable spa standby power.  Portable electric spa standby power shall not be greater than 5(V2/3) watts where V = the total volume, in gallons, when spas are measured in accordance with the spa industry test protocol.

403.9.2 Time switches. Time switches shall be installed on swimming pool heaters and pumps that can automatically turn off and on the heaters and pumps off and on according to a preset schedule shall be installed on swimming pool heaters and pumps.

Exceptions:

1. Where public health standards require 24-hour pump operation.

2. Where pumps are required to operate solar- and waste-heat-recovery pool heating systems.

403.9.3 Pool covers. Heated swimming pools and spas shall be equipped with a vapor-retardant pool cover on or at the water surface. Pools heated to more than 90°F (32°C) shall have a pool cover with a minimum insulation value of R-12.

Exception: Outdoor pPools deriving over 70 60 percent of the energy for heating from site-recovered energy or solar energy source computed over an operating season.

403.9.4 Pool design.

403.9.4.1 Pool pump motors.  Pool pump motors shall meet the following criteria:

1.  Pool pump motors shall not be split-phase, shaded-pole or capacitor start-induction run types.

2.  Pool pumps and pool pump motors with a total horsepower (HP) of ≥ 1 HP shall have the capability of operating at two or more speeds. The low speed shall have a rotation rate of no more than ½ of the motor’s maximum rotation rate.

3.  Pool pumps motor controls shall have the capability of operating the pool pump at a minimum of two speeds. The default circulation speed shall be the residential filtration speed, with a higher speed override capability for a temporary period not to exceed one normal cycle or 120 minutes, whichever is less.

Exception:  Solar pool heating systems shall be permitted to run at higher speeds during periods of usable solar heat gain.

SECTION 404

ELECTRICAL POWER AND LIGHTING SYSTEMS

404.1 Lighting equipment (Prescriptive). A minimum of 50 percent of the lamps in permanently installed lighting fixtures shall be high-efficacy lamps.

SECTION 405

SIMULATED PERFORMANCE ALTERNATIVE (Performance)

405.1 Scope. This section establishes criteria for compliance using simulated energy performance analysis. Such analysis shall include heating, cooling, and service water heating energy only.

405.2 Mandatory requirements. Compliance with this section requires that the mandatory provisions identified in Section 401.2 be met. All supply and return ducts not completely inside the building thermal envelope shall be insulated to a minimum of R-6.

405.2.1 Ceiling insulation. Ceilings shall have an insulation level of at least R-19, space permitting. For the purposes of this code, types of ceiling construction that are considered to have inadequate space to install R-19 include single assembly ceilings of the exposed deck and beam type and concrete deck roofs. Such ceiling assemblies shall be insulated to at least a level of R-10.

405.3 Performance-based compliance. Compliance based on simulated energy performance requires that a proposed residence (proposed design) be shown to have an annual normalized, modified energy load that is less than or equal to the annual energy load of the standard reference design. code official, such as the Department of Energy, Energy Information Administration’s State Energy Price and Expenditure Report. Code officials shall be permitted to require time-of-use pricing in energy cost calculations.

405.4 Documentation.

405.4.1 Compliance software tools. Documentation verifying that the methods and accuracy of tThe Energy Gauge USA Fla/Res compliance software tools shall be utilized to conform to the provisions of this section. shall be provided to the code official. Compliance software provisions and overall stringency shall be as described in Normative Appendix B.

405.4.2 Compliance report. The cCompliance software tools shall generate a Form 405 report that documents that the proposed design complies with Section 405.3. The compliance documentation shall be submitted to the building official before a building permit is issued and shall include the following information:

1. Address or other identification of the residence;

2. An inspection checklist documenting the building component characteristics of the proposed design as listed in Appendix B,Table B-1.1.2(1) 405.5.2(1). The inspection checklist shall show results for both the standard reference design and the proposed design, and shall document all inputs entered by the user necessary to reproduce the results;

3. Name of individual completing the compliance report; and

4. Name and version of the compliance software tool.

Exception: Multiple orientations. When an otherwise identical building model is offered in multiple orientations compliance for any orientation shall be permitted by documenting that the building meets the performance requirements in each of the four cardinal (north, east, south and west) orientations.

405.4.3 Additional documentation. The code official shall be permitted to require the following documents:

1. Documentation of the building component characteristics of the standard reference design.

2. An EPL Display Card certification signed by the builder providing the building component characteristics of the proposed design (as given in Table 405.5.2(1)) shall be provided to the purchaser of the home at time of title transfer.

3. Documentation of the component efficiencies actual values used in the software calculations for the proposed design.

405.5 Calculation requirements for glazing.

405.5.1 Glass areas. All glazing areas of a residence, including windows, sliding glass doors, glass in doors, skylights, etc. shall include the manufacturer’s frame area in the total window area. Window measurements shall be as specified on the plans and specifications for the residence.

Exception: When a window in existing exterior walls is enclosed by an addition, an amount equal to the area of this window may be subtracted from the glazing area for the addition for that overhang and orientation.

405.5.2 Overhangs. Overhang effect is measured by Overhang Separation, which is the vertical measure of the distance from the top of a window to the bottom of the overhang.  The overhang for adjustable exterior shading devices shall be determined at its most extended position. Nonpermanent shading devices such as canvas awnings shall not be considered overhangs. Permanently attached wood and metal awnings may be considered overhangs.

405.5.3 Doors with glazing. For doors that are opaque or where the glass is less than one-third of the area of the door, the total door area shall be included in the door calculation.  For unlabeled sliding glass doors or when glass areas in doors is greater than or equal to one-third of the area of the door, the glazing portion shall be included in the glazing calculation and the opaque portion of the door shall be included in the door calculation. When glass area in doors is greater than or equal to one-third of the area of the door, the door shall be included in the glazing calculation as a total fenestration using the tested U-factor and solar heat gain coefficient.

405.6 Requirements specific to credit options.  Credit may be claimed in the software compliance calculation for technologies that meet prescriptive criteria specified below for various options.

405.6.1 Installation criteria for homes claiming the radiant barrier option. The sheet radiant barrier or IRCC options may be claimed where the radiant barrier system is to be installed in one of the configurations depicted in Figure 405.6.1 and the following conditions are met:

1.  It shall be fabricated over a ceiling insulated to a minimum of R-19 with conventional insulation and shall not be used as a means to achieve partial or whole compliance with a minimum attic insulation level of R-19. Either a sheet type or spray applied interior radiation control coating (IRCC) may be used.

2.  If the radiant barrier material has only one surface with high reflectivity or low emissivity it shall be facing downward toward the ceiling insulation.

3. The attic airspace shall be vented in accordance with Section R806 of the Florida Building Code, Residential.

4.  The radiant barrier system shall conform to ASTM C 1313, Standard Specification for Sheet Radiant Barriers for Building Construction Applications, or ASTM C 1321, Standard Practice for Installation and Use of Interior Radiation Control Coating Systems (IRCCS) in Building Construction as appropriate for the type of radiant barrier to be installed. The operative surface shall have an emissivity not greater than 0.06 for sheet radiant barriers or 0.25 for interior radiation control coatings as demonstrated by independent laboratory testing according to ASTM C 1371.

5.  The radiant barrier system (RBS) shall conform with ASTM C 1158, Use and Installation of Radiant Barrier Systems (RBS) in Building Constructions for Sheet Radiant Barriers, or ASTM C 1321, Standard Practice for Installation and Use of Interior Radiation Control Coating Systems (IRCCS) in Building Construction for IRCC systems.

6.  The radiant barrier shall be installed so as to cover gable ends without closing off any soffit, gable or roof ventilation.

FIGURE 405.6.1

ACCEPTABLE ATTIC RADIANT BARRIER CONFIGURATIONS

[No change to figure]

405.6.2  Installation criteria for homes claiming the cool roof option. The  cool roof option may be claimed where the roof to be installed has a tested solar reflectance of greater than 4 percent when evaluated in accordance with ASTM methods E-903, C-1549, E-1918 or CRRC Method #1. Emittance values provided by the roofing manufacturer in accordance with ASTM C 1371 shall be used when available.  In cases where the appropriate data are not known, emittance shall be the same as the Standard Reference Design. Testing of a qualifying sample of the roofing material shall be performed by an approved independent laboratory with these results provided by the manufacturer.

405.6.3 Installation criteria for homes using the unvented attic assembly option. The unvented attic assembly option may be used if the criteria in Section R806.4 of the Florida Building Code, Residential, have been met.

405.6.4 Installation criteria for homes using the cross ventilation option.  The cross ventilation option may be used if the following criteria have been met.

1. Operable aperture areas totaling a minimum of 12 percent of the floor area of the room shall be provided for all primary living areas and main bedrooms.

2. Insect screens shall be provided for all windows and doors to be considered operable aperture area. All screened entry doors and interior doors in the ventilated areas shall be provided with either (1) mechanically attached door stops (or similar devices) to hold the door in an open position or (2) operable louvers.

3. The total aperture area shall be provided by a minimum of two distinct windows. Each window shall provide not more than 70 percent of the total aperture area. The windows (or sliding glass doors) shall be placed in adjacent or opposite walls. The windows may be placed on a single outside wall if wing walls are used.

4. Where wing walls are included in the building design for ventilation purposes, they shall be placed between windows to create a high-pressure and a low-pressure zone on each window. Wing walls shall extend from the ground to eve height, be located on the windward side of the building, and extend outward from the building a distance at least equal to one-half the width of the window. NOTE: This technique is effective only for areas which experience significant and continuous winds during the cooling months.

405.6.5 Installation criteria for homes using the whole house fan option.  The whole house fan option may be used if the following criteria have been met.

1. The whole house fan has been sized to provide a minimum of 20 air changes per hour for the entire house.

2. The fan installed shall have a free air cfm rating of at least three times the square footage of the conditioned area of the house.

3. To ensure adequate air exhaust, the house attic shall have gable, ridge or wind turbine vents whose total opening area is equal to four times the ceiling cutout area for the whole house fan. Soffit vents shall not be included in the exhaust vent area.

405.6.6 Installation criteria for homes claiming the heat recovery unit (HRU) option.  The heat recovery unit option may be used for installation of a waste heat recovery unit (HRU) on either an air conditioner or a heat pump where the heat recovery unit has a minimum net useful heat exchange effect of 30 percent and meets the following criteria:

1. The net useful heat exchange effect shall be demonstrated by either a Form ___ prominently displayed on the unit with test results clearly visible for inspection or by an ARDM certified refrigerant desuperheater seal affixed to the unit.

2. The net useful heat exchange effect shall have been determined by an independent laboratory testing to the standard rating conditions specified in Florida Standard FL-1 (see Appendix D).

3. If more than one air conditioning system is installed in a residence and only one HRU is installed, energy load shall be based on the gallon capacity of the water heater to which it is coupled and the total capacity of the water heaters in the residence.  In such case, the HRU shall be attached to the system serving the daytime primary living areas (family room, living room, kitchen, dining room and adjacent bedrooms and bathrooms).

405.6.7 Installation criteria for homes claiming the dedicated heat pump option.  The dedicated heat pump option may be used for a dedicated heat pump (also known as a heat pump water heater) installed either with a tank (an integral unit) or without tank (add on to another water heater) based on the COP of the system on which it is installed.  No minimum rating is required for this equipment.